# DEPARTMENT OF HOMELAND SECURITY

# UNITED STATES COAST GUARD

# ENGINEERING SERVICES DIVISION

# SPECIFICATIONS

# FOR

# REPLACE HVAC

U.S. COAST GUARD

STATION OREGON INLET

BODIE ISLAND, NC

JANUARY 2018

COMMANDING OFFICER

UNITED STATES COAST GUARD

CIVIL ENGINEERING UNIT, RM 2179

1240 EAST NINTH STREET

CLEVELAND, OHIO 44199-2060

AUTHOR:  GARY E. WHITTAM                                                         DIV 1 - 26

TABLE OF CONTENTS

| Division | Section | Title | Page |
| --- | --- | --- | --- |
| 1 |  | GENERAL REQUIREMENTS |  |
|  | 01 11 00 | Scope of Work | 5 |
|  | 01 11 16 | Work by Others | 5 |
|  | 01 12 16 | Project Phasing | 6 |
|  | 01 14 00 | Contractor Work Hours | 6 |
|  | 01 14 13 | Pre-bid Site Visits | 7 |
|  | 01 14 14 | Pre-Construction Site Conditions | 7 |
|  | 01 14 16 | Coordination | 8 |
|  | 01 14 19 | Field Adjustments | 8 |
|  | 01 18 13 | Utility Permits | 8 |
|  | 01 18 14 | Building Permits | 9 |
|  | 01 18 17 | Environmental Permits | 9 |
|  | 01 26 13 | Request for Information | 9 |
|  | 01 31 19 | Project Meetings | 11 |
|  | 01 32 16 | Construction Schedule, Schedule of Values and Progress Schedule | 11 |
|  | 01 32 26 | Construction Daily Reports | 12 |
|  | 01 33 00 | Submittal Procedures | 13 |
|  | 01 35 29 | Safety Program | 15 |
|  | 01 51 00 | Temporary Utilities | 16 |
|  | 01 51 13 | Equipment/Utility Lockout and Tagout Requirements | 17 |
|  | 01 51 16 | Temporary Fire Protection | 17 |
|  | 01 54 30 | Confined Entry | 18 |
|  | 01 55 00 | Access Roads and Parking | 18 |
|  | 01 55 29 | Staging Areas and Access | 18 |
|  | 01 56 00 | Lights, Signs & Barricades | 19 |
|  | 01 57 13 | Erosion and Sediment Control | 19 |
|  | 01 57 23 | Pollution Control | 20 |
|  | 01 65 00 | Recovered Materials Notice | 21 |
|  | 01 66 13 | Hazardous Waste | 21 |
|  | 01 66 16 | Safety Data Sheets and Material Handling Procedures | 22 |
|  | 01 71 33 | Protection from Weather and Construction Operations | 22 |
|  | 01 74 00 | General Cleanup and Site Restoration of Work Areas | 23 |

# TABLE OF CONTENTS (cont.)

| Division | Section | Title | Page |
| --- | --- | --- | --- |
| 1 |  | GENERAL REQUIREMENTS (cont.) |  |
|  | 01 78 00 | As Built Drawings | 23 |
|  | 01 78 23 | Operating Instructions and Training | 24 |
|  | 01 80 00 | Facility Preventative Maintenance Program | 24 |
|  |  | List of Submittals | 26 |
|  |  | Contract Item Acceptance Request | 30 |
| 2 |  | EXISTING CONDITIONS |  |
|  | 02 41 19 | Demolition And Removal | 31 |
| 7 |  | THERMAL AND MOISTURE PROTECTION |  |
|  | 07 21 16 | Mineral Fiber Blanket Insulation | 38 |
|  | 07 27 36 | Spray Foam Air Barriers | 43 |
|  | 07 92 00 | Joint Sealants | 61 |
| 9 |  | FINISHES |  |
|  | 09 29 00 | Gypsum Board | 69 |
|  | 09 51 00 | Acoustical Ceilings | 77 |
|  | 09 90 00 | Paints and Coatings | 84 |
| 22 |  | PLUMBING |  |
|  | 22 00 00 | Plumbing, General Purpose | 99 |
| 23 |  | HEATING, VENTILATING, AND AIR CONDITIONING |  |
|  | 23 00 00 | Air Supply, Distribution, Ventilation, and Exhaust Systems | 130 |
|  | 23 03 00 | Basic Mechanical Materials and Methods | 143 |
|  | 23 05 93 | Testing, Adjusting, and Balancing for HVAC Systems | 147 |
|  | 23 07 00 | Thermal Insulation for Mechanical Systems | 158 |
|  | 23 09 53 | Space Temperature Control Systems | 171 |
|  | 23 23 00 | Refrigerant Piping | 187 |
|  | 23 81 00 | Variable Refrigerant Flow Systems | 200 |
|  | 23 81 01 | Unitary Air Conditioning Equipment | 208 |

# TABLE OF CONTENTS (cont.)

| 26 |  | ELECTRICAL |  |
| --- | --- | --- | --- |
|  | 26 00 00 | Basic Electrical Materials and Methods | 217 |
|  | 26 20 00 | Electrical Distribution System | 223 |

DIVISION 1

(May 2019 Version)

# SECTION 01 11 00

SCOPE OF WORK

1.	WORK INCLUDED:  Major items of work shall include the following:

1.1	The scope of the project is to provide a major renovation of the heating, ventilating, & air conditioning (HVAC) systems in the Multi-Purpose Building and Shop Building.  Both buildings will be occupied during the renovation work and will requiring phasing of the demolition and construction work to maintain U.S. Coast Guard operations.  For the shop building, the existing hot water heating system and air conditioning/ventilation systems will be removed.  For the Multi-Purpose Building, the existing split systems, ductwork and associated controls will be removed.  Two (2) 16-ton and one (1) 18 ton variable refrigerant system and associated controls shall be installed in the Multi-Purpose building with individual indoor units to serve the offices and berthing rooms. Additionally, the contractor shall replace existing oil-fired water heater with electric water heater and perform some building envelope improvements related to attic insulation and insulation under the buildings.  A single 2-ton multi-zone system and two (2) 3-1/2-ton heat pump constant volume systems shall be installed in the Shop building.  For all equipment removed in this project, the contractor shall remove and capture all Class ODS refrigerants in accordance with the Clean Act Amendment of 1990.  The contractor will be required to maintain operations of the U.S. Coast Guard and will be required to performed the work in separate phases and provide temporary cooling and heating systems of affected systems.

1.2	Work associated with these items is described in the following specification sections and/or are shown on the contract drawings.  Incidental work items not listed above and necessary for completing the project shall be included.

2.	DRAWINGS:  Drawings and the accompanying specifications are the property of the Government and comprise legal documentation that pertains exclusively to this project.  Drawings will be made available in a format determined by the solicitation method.  CEU Cleveland will not provide hard copies of drawings.

| 2.1 Construction Drawings: | CG DWG. C8454 sheets 1 thru 32 of 32 |
| --- | --- |
| 2.2 Reference Documents: | USCG Approved Equipment Enrollment Catalog |
|  | Equipment Enrollment Form(s) |

# SECTION 01 11 16

WORK BY OTHERS

1.	Work not included in the Contract:  Non-contractor personnel will accomplish the following work items necessary for completion of the project. However, the contractor must coordinate accomplishment of these work items with the appropriate parties noted below in accordance with Section 01 14 16, “Coordination”.

1.1	Work by Utility Companies:  Utility company service crews will perform all electrical, water, natural gas, and/or sewer connections to main service lines.  The contractor shall ensure that all main electrical service panels and accompanying feeders /sewer and water line drops are completed and ready for service prior to coordinating any tie in as indicated on the drawings.

1.2	Work by other Contractors or Service Companies: Contractor personnel and equipment associated with another construction contract in progress may require access to the site during execution of this contract.  The contractor shall coordinate work and ensure that work operations do not interfere with the contract currently in progress.  The contractor shall allow service contract personnel access to the site for trash removal, snow removal, grounds maintenance or the performance of other related service contracts.  The Coast Guard will advise the contractor of the trash removal, grounds maintenance or other recurring maintenance schedules.

# SECTION 01 12 16

PROJECT PHASING

1.	To minimize interference with Coast Guard operations, utilize the following phasing sequence to accomplish contract work. Coordinate timing between successive phases with Coast Guard personnel to allow for continued operation of USCG in the area during construction.  Provide temporary cooling and heating in the areas of work affected during construction.  Submit a Project Phasing Plan for review that reflects the following phases:

PHASE I – Multi-Purpose Building, 1st floor: All work located on the first floor of the Multi-Purpose Building shall be performed during this phase of the project.  Only one system can be worked on at a time during this phase of the work to minimize the impact on USCG operation.  Temporary cooling and heating will be required during the work performed on the first floor.  The building’s galley can only be shut down for a period of one week during the phase of work.

PHASE II – Multi-Purpose Building, 2nd floor: All work located on the second floor of the Multi-Purpose Building shall be performed during this phase of the project.  Only 3 Berthing Rooms can be worked on at a time during this phase of the work to minimize the impact on USCG operation.

PHASE III – Shop Building: All work located in the Shop Building shall be performed during this phase of the project.  Only one system can be worked on at a time during this phase of the work to minimize the impact on USCG operation.  Temporary cooling and heating will be required during the work performed in the Shop Building.

# SECTION 01 14 00

CONTRACTOR WORK HOURS

1.	WORK HOURS:  Accomplish work during normal unit operational hours of 7:30 a.m. to 4:30 p.m., Monday through Friday unless otherwise approved by the Coast Guard.  Note any departures from these work hours on the Daily Reports.

2.	SATURDAY, SUNDAY AND HOLIDAYS:  The contractor shall provide the Contracting Officer's Representative at least forty-eight hours advance notice prior to working on weekends or Federal holidays.  The Government may reject any such request without impacting the completion time of the contract.

3.	CONTRACT COMPLETION:  The contractor shall complete work within the time frame indicated upon issuance of the Notice to Proceed. Limitations imposed by these work hours will not entitle the Contractor additional time to complete the project. Refer to FAR Clause 52.211-10 "Commencement, Prosecution and Completion of Work".

SECTION 01 14 13

PRE-BID SITE VISITS

1.	GENERAL:  Bidders are responsible for visiting the site to field verify existing conditions and determine actual dimensions and the nature of the work required. Failure to visit the site does not relinquish the bidder from determining the extent and scope of the work required and estimating the difficulty and cost to complete the project. Requests for equitable adjustments, in either time or money, arising from failing to field verify site conditions may be denied. Provisions regarding the site visit requirements are outlined in FAR Clause 52.236-3 “Site Investigation and Conditions Affecting the Work”.

2.	SITE VISIT:  Arrange pre-bid site visits to verify existing conditions with MK1 Joel Gibney, Engineer Petty Officer, U.S. Coast Guard Station Oregon Inlet at (252) 441-6260 or joel.m.gibney@uscg.mil. The Engineer Petty Officer may limit hours of access or levy certain restrictions regarding visits to the site.

# SECTION 01 14 14

PRE-CONSTRUCTION SITE CONDITIONS

1.	SITE CONDITION VERIFICATION:  The Contractor shall verify the conditions of the existing site, equipment and facilities potentially affected by the work under this contract and photograph and/or videotape the conditions in order to document their pre-construction condition.  Copies of the photos and videos shall be submitted to the Contracting Officer prior to starting work.

2.	UTILITIES:  The contractor shall use proactive measures such as digging, metering, testing, underground utility location devices, and utility company location services to locate all underground utilities identified in the area of work at no additional expense to the Government.  Additional cost of unplanned outages and repair of damaged utilities, including emergency repairs by others, not properly identified by the Contractor shall be the Contractor’s responsibility.

# SECTION 01 14 16

COORDINATION

1.	INTERFERENCE WITH COAST GUARD OPERATIONS: Accomplish work in a manner that causes minimal impact on normal operations.  The Contractor shall notify the Contracting Officer’s Representative at least five working days in advance of any planned outages of water, electrical, telephone, or sanitary facilities. Notify the Contracting Officer’s Representative at least one week prior to beginning construction.

2.	MILITARY STATION REGULATIONS:

2.1	The Contractor, his employees, and subcontractors shall become familiar with and obey all station regulations.  All personnel employed on the project shall keep within the limits of the work and avenues of ingress and egress, and shall not enter any other areas outside of the site of the work unless required to do so in the performance of their duties.  The Contractor's equipment shall be conspicuously marked for identification.

2.2	There shall be NO SMOKING in any Coast Guard building.

2.3	Storage Areas: The Contracting Officer’s Representative will determine exact location and boundaries of staging areas.  Under no circumstances shall materials be stored in areas that will interfere with aircraft operations.

2.4	Storm Protection: If a gale force wind warning or higher is issued, take precautions to minimize any danger to persons and protect the work and nearby Government property.  Precautions shall include, but not be limited to, closings, removing loose materials, tools and equipment, from exposed locations.  Remove and secure scaffolding and temporary work.  Close openings in the work area if storms of lessor intensity are imminent.

# SECTION 01 14 19

FIELD ADJUSTMENTS

1.	The Contracting Officer’s Representative may authorize field adjustments.  Field adjustments are those alterations that do not affect time, price, or intent of the contract documents.  All field adjustments shall be documented in the Daily Reports and on the As-Built Drawings.

# SECTION 01 18 13

UTILITY PERMITS

1.	The Contractor is responsible for obtaining all permits required for connection to all public or private utility systems.  This shall include all permit, inspection, administrative and accessory costs normally charged of customers by the utility.

1.1	All Tie-in and/or connection fees will be paid by the Contractor.

# SECTION 01 18 14

BUILDING PERMITS

1.	NO BUILDING PERMITS from state or local governments are required for work performed on federal property.  Courtesy permits may be obtained at the Contractor's option.  No payment will be made to the Contractor for any permit cost.  Design changes to obtain courtesy permits, even at no cost, will not be allowed without written approval of the Contracting Officer.

# SECTION 01 18 17

ENVIRONMENTAL PERMITS

1.	Unless directed by other sections of this specification, the Contractor will not be responsible for obtaining environmental permits.

SECTION 01 26 13

REQUESTS FOR INFORMATION

1.	SUMMARY:

A.  Section Includes:  Administrative requirements for requests for information.

2.	DEFINITIONS:

A.  Request for Information:  A document submitted by the Contractor requesting clarification of a portion of the contract documents, hereinafter referred to as RFI (Request for Information).

B.  Proper RFIs:  A properly prepared request for information shall include a detailed written statement that indicates the specific Drawings or Specification in need of clarification and the nature of the clarification requested.

1.  RFIs shall be sequentially numbered.

2.  Drawings shall be identified by drawing number and location on the drawing			sheet.

3.  Specifications shall be identified by Section number, page and paragraph.

C.  Improper RFIs:  RFIs that are not properly prepared.

1.  Improperly prepared RFIs will not be processed by the Contracting Officer, but will be returned unprocessed.

D.  Frivolous RFIs:  RFIs that request information that is clearly shown on the Contract Documents.

1.  Frivolous RFIs may be returned unprocessed.

3.	CONTRACTOR’S REQUESTS FOR INFORMATION:

A.  When the Contractor is unable to determine from the Contract Documents, the material, process or system to be installed, the Contracting Officer shall be requested to make a clarification of the indeterminate item.

1.  Wherever possible after contract award, such clarification shall be requested at the next site visit by the Contracting Officer’s Representative (COR), with the response entered on the daily reports. When clarification at the COR’s site visit is not possible either because of the urgency of the need, or the complexity of the item, Contractor shall prepare and submit an RFI to the Contracting Officer.

B.  Contractor shall endeavor to minimize the number of RFIs.  In the event that the process becomes unwieldy, in the opinion of the Contracting Officer because of the number and frequency of the RFIs submitted, the Contracting Officer may require the Contractor to abandon the process and submit future requests as either submittals, substitutions or requests for change.

C.  RFIs shall be submitted on the form provided by the Contracting Officer.  Forms completely filled in, and if prepared by hand, shall be fully legible after photocopying or fax transmission.  Each page of the attachments to RFIs shall bear the RFI number in the upper right corner.

D.  RFIs shall be originated by the Prime Contractor.

1.  RFIs from subcontractors or material suppliers shall be submitted through, reviewed by, and signed by the Prime Contractor prior to submitting to the Contracting Officer.

2.  The Contracting Officer will neither act on nor respond to RFIs received directly from subcontractors or suppliers.

E.  Contractor shall carefully study the Contract Documents to assure that the requested information is not available therein. RFIs which request information available in the Contract Documents will be deemed either Improper or Frivolous as defined above.

F.  In cases where RFIs are issued to request clarification of coordination issues, for example, pipe and duct routing, clearances, specific locations of work shown diagrammatically, and similar items when feasible, Contractor shall fully lay out a suggested solution using drawings or sketches drawn to scale, and submit with the RFI.

G.  RFIs shall not be used for the following purposes:

1.  To request approval of submittals.

2.  To request approval of substitutions.

3.  To request changes which entail additional cost or credit.

4.  To request different methods of performing work than those drawn and specified.

H.  In the event the Contractor believes that a clarification by the Contracting Officer results in additional cost or time, the Contractor shall not proceed with the work indicated by the RFI until a modification is prepared and approved.  RFIs do not automatically justify a cost increase in the work or a change in the project schedule.

1.  Answered RFIs shall not be construed as approval to perform extra work.

I.  Contractor shall prepare and maintain a log of RFIs, and at any time requested by the Contracting Officer, Contractor shall furnish copies of the log showing outstanding RFIs.   Contractor shall note unanswered RFIs in the log.

J.  Contractor shall allow up to 14 days review and response time for RFIs, however, the Contracting Officer will endeavor to respond in a timely fashion to RFIs.

K.  The Government reserves the right to issue a change order to expedite the work per FAR Clause 52.243-4, Changes.

4.	CONTRACTING OFFICER’S RESPONSE TO RFIs:

A.  Contracting Officer will respond to RFIs on one of the following forms:

1.  Proper RFIs:

a.  Change Order

b.  Request for Proposal

2.  Improper or Frivolous RFIs:

a.  Unprocessed RFIs will be returned with a stamp or notation:  Not

Reviewed.

3.  Answers to properly prepared RFIs may be made directly upon the RFI form with supplementary instructions as necessary.

# SECTION 01 31 19

PROJECT MEETINGS

1.	LOCATION:  Project meetings will be conducted either on-site or with a conference call.  The following meetings may be held:

1.1	Pre-Construction Conference:  After award of a contract, the Coast Guard will arrange a conference with the contractor, and necessary Coast Guard personnel.  The purpose of this conference is to orient the Contractor to Government procedures for wage rates, contractual and administrative matters, and to discuss specific issues regarding actual construction.

1.2	Progress and Technical Review Meetings:  These meetings generally take place at the project site.  Either party may request a meeting to review the progress of the project and/or review or clarify the technical requirements of the specifications.

SECTION 01 32 16

CONSTRUCTION SCHEDULE, SCHEDULE OF VALUES,

AND PROGRESS SCHEDULE

1.	In accordance with the Notice to Proceed letter, the Contractor shall submit the following:

a.  Construction Schedule-This schedule shall be prepared using a horizontal bar graph with time scale.  It shall be in an industry accepted Project Management format and shall accurately display:

1.  All major categories of work to be performed within the required contract completion date broken out in sufficient detail to track progress throughout the life of the contract.  Major work categories should include but are not limited to mobilization, carpentry, plumbing, mechanical, electrical, roofing, concrete, site work, and demobilization.  In addition to construction activities, procurement times for critical items, submittal turnaround time, mobilization, final inspection, punchlist work, and demobilization shall be shown on the schedule.

2.  The duration of each work category.

3.  Any concurrent work categories.

b.  Schedule of Values-This schedule shall be prepared as a detailed cost breakdown of the contract price and be submitted with the Construction Schedule.  This schedule shall include but not be limited to costs of materials, equipment, and labor for all major work categories shown on the Construction Schedule.  The Contractor shall adhere to the following guidelines when developing the Schedule of Values.

1.  Format - The line items in the Schedule of Values shall be the same as that of the Construction Schedule.

2.  Bonds - Bonding costs will only be paid in a lump sum if they are broken out separately and included with the schedule of values.  The Contractor shall provide evidence that he has furnished full payment to the surety.

3.  Materials - To request progress payments for materials delivered to the construction or fabrication site, the particular category of work associated with the materials must be broken down into separate material and labor costs.

2.	UPDATES:  Each month and /or with each progress payment request, the Contractor shall submit the following:

a.  Progress Schedule-This schedule shall be an update of the Construction Schedule.  It shall show the current schedule of all work.

1.  Modifications - If modifications are made to the contract, the work added shall be tracked separately from the original Construction Schedule and shall maintain its individuality on the Progress Schedule throughout the life of the contract.   Progress Payment requests shall not lump modification costs into the original contract price.

SECTION 01 32 26

CONSTRUCTION DAILY REPORTS

1.	GENERAL:  The Contractor shall complete a Daily Report for each and every day after mobilization.  The importance of an accurate, fully detailed Daily Report, promptly delivered to the designated On-Site Representative cannot be overemphasized.  The report shall provide an accurate cumulative summary of the history and performance of the work.  The Daily Report shall document weather; work hours; work in-place; inspections and tests conducted, and their results; dimensional checks; equipment and material checks; data on workers by classification; the mobilization and demobilization of construction equipment; materials delivered to the site; and any other pertinent noteworthy event; e.g., personnel injury, site visit by Coast Guard personnel, etc.

2.	RESPONSIBILITY:  The Daily Reports play an important role in settling disputes and claims for both parties.  For this reason the On-Site Representative and the Contractor's Superintendent, together, should review the report to ensure its completeness and accuracy.  Each day's report shall be submitted to the On-Site Representative no later than 10:00 a.m. the following morning.  The maximum allowable retainage will be enforced for late, sporadic or non-submission of Daily Reports.  In the absence of an On-Site Representative the Contractor shall mail the Daily Reports directly to the Contracting Officer every Friday.  Should the Daily Report indicate an accident, environmental issue, OSHA violation or any crisis the On-Site Representative deems important, the Report should be faxed immediately to the Contracting Officer at (216) 902-6278.

3.	DESIGNATED ON-SITE REPRESENTATIVE RESPONSIBILITY:  After a Notice to Proceed for site work has been issued the On-Site Representative shall complete a Daily Report for each day until the Contractor mobilizes.  After the Contractor is at the site, the On-Site Representative shall ensure that the Contractor completes the Daily Report in accordance with Paragraphs 1 and 2 above.  Any items of dispute or other notes the On-Site Representative feels appropriate shall be added to the Daily Report.  The On-Site Representative is also responsible for informing the COR when the contractor fails to submit daily reports.

SECTION 01 33 00

SUBMITTAL PROCEDURES

1.	GENERAL:  The Contractor shall submit to the Contracting Officer (4) copies of submittals required by this specification and/or itemized on the "List of Submittals" found at the end of this division.

2.	REQUEST:  A "CONTRACT ITEM ACCEPTANCE REQUEST" shall accompany all submittals.  All items shall be individually listed and clearly identified, referencing the applicable Section and Paragraph.  A copy of this form is located at the end of this division and may be reproduced as needed.

2.1	Up to eight (8) items may be listed on an individual acceptance request.  Number each Contract Item Acceptance Request consecutively (Submittals # 1, 2, etc.) and re-submittals with letters (Submittal #1A is the first re-submittal of Submittal #1).

2.2	Submittals shall be forwarded to the Contracting Officer.  The contractor shall allow 14 calendar days, excluding mailing time, for the review process in the Construction Schedule and all project planning.  In instances where submittal review must be expedited, the Contractor may annotate the Contract Item Acceptance Request as "Urgent" and provide a FAX number for prompt return.  The Coast Guard will make every effort to accelerate the review of each urgent submittal; however, the Contractor should not anticipate a reduced time schedule and shall plan project progress accordingly.

3.	DEVIATIONS

3.1	Deviation from specification:

3.1.1	The Contracting Officer will consider requests for deviations/substitutions only if submitted within fifteen (15) calendar days after award.

3.1.2	Deviations may be considered when a product becomes unavailable through no fault of the Contractor.

3.1.3	The Contractor shall document each request with complete data substantiating compliance of proposed deviation with the Contract documents.  Request for deviation shall not be submitted on a Request for Information (RFI) form.

3.1.4	A request constitutes a representation that the Contractor:

3.1.4.1	Has investigated proposed product and determined that it meets or exceeds quality level of specified product.

3.1.4.2	Will provide the same warranty for deviation as for specified product.

3.1.4.3	Will coordinate installation and make changes to other work which may be required for the work to be completed at no additional cost to the Government.

3.1.4.4	Waives claims for additional costs or time extension which may subsequently become apparent.

3.1.4.5	Will reimburse the Government for review or redesign services associated with re-approval by the Contracting Officer.

3.1.5	If the deviation has a lesser value than the product originally specified, the Contractor shall provide a credit to the Government.

3.1.6	Deviations will not be considered when they are indicated or implied on Shop Drawings or Product Data submittals, without a separate written request, or when acceptance will require revisions to the Contract documents.

3.2	Deviation submittal procedures:

3.2.1	The Contractor shall mark the “Deviation” block on the Contract Item Acceptance Request (CIAR) form and provide the information stated in Paragraph 3.1.

3.2.2	The Contractor shall submit shop drawings, product data, and certified test results attesting to proposed product equivalence.  Burden of proof is on the Contractor.

3.2.3	The Contracting Officer will then review the “deviation” request and either accept or reject the deviation.  The Contracting Officer’s acceptance of the deviation signifies that the Contractor has provided the information required in Paragraph 3.1.   If a credit is due the government, the Contracting Officer will notify the Contract Specialist and the deviation will be processed utilizing the Change Request procedures for a modification to the contract/task order.

3.2.4	The Contracting Officer will notify the Contractor of acceptance/rejection of the deviation via an accepted or rejected CIAR.   The Contracting Officer will notify the Contractor, in writing, if a modification to the contract is required.

3.2.5	If a request for deviation is received without the documentation stated above, the Contracting Officer will return the submittal to the contractor for the required information.

4.	ACCEPTANCE:  Submittals will be stamped "Accepted," "Accepted with Comments," or "Resubmit".  Acceptance, Acceptance with comments or Resubmit for each item will be indicated on the Contract Item Acceptance Request form and one copy returned to the Contractor.

4.1	Prompt re-submittal of items is required.  The Contractor shall furnish a new Contract Item Acceptance Request numbered in accordance with the requirements of paragraph 2.1.

5.	DEFECTIVE WORK: Acceptance of Submittals does not restrict the Government's right to reject departures from contract requirements, use of damaged or improperly installed items/materials, or latent defects, nor does it prejudice the Government's rights of rejecting any work found defective at Final Inspection and Acceptance.

5.1	Work started or completed prior to submittal acceptance is solely at Contractor's risk and may jeopardize contract performance.

SECTION 01 35 29

SAFETY PROGRAM

1.	GENERAL:  The Contractor is wholly responsible for work site safety.  The Contractor shall implement a safety program that protects the lives and health of personnel in the construction area, prevents damage to property, and avoids work interruptions.  The Contractor shall provide appropriate safety barricades, signs, signal lights, etc. (see Section 01 56 00, “Lights, Signs & Barricades”) as well as complying with the requirements of all applicable Federal, State and Local safety laws, rules and regulations.

2.	COMPLIANCE:  The Contractor is specifically required to comply with the requirements of the U. S. Army Corps of Engineers "Safety and Health Requirements Manual" (EM 385-1-1, latest version available) and the “Accident Prevention” clause (FAR 52.236-13).  Once accepted, this safety plan shall become part of the contract requirements.  Note:  This review/acceptance does not in any way relinquish the Contractor from responsibility for work site safety nor the obligation to comply with the OSHA regulations found in 29 CFR 1910 & 1926 or any other State or Local safety law, rule or regulation applicable to the contract work.  The Coast Guard will cooperate fully with the Department of Labor (Occupational Safety and Health Administration) in their enforcement of OSHA regulations.

3.	SAFETY PLAN: The Contractor shall submit a written safety plan.  At a minimum, this plan shall describe the Contractor's general safety program and identify specific safety provisions for hazards incidental to the contract work; e.g., elevated working surfaces, working over water, working from floating work platforms, overhead crane operations, etc.

SECTION 01 51 00

TEMPORARY UTILITIES

1.	GENERAL:  All temporary utility connections shall be compatible with existing materials and equipment to provide safe and efficient installation, operation and removal.  There are no utilities available on site.  The contractor shall provide portable generation, water, portable toilets and other services necessary to complete the project.

2.	ELECTRICITY AND WATER: Electrical power and water are available on the site.  The Contractor will be permitted to utilize these utilities in performing the work, provided that the existing systems are not overloaded.  The Contractor is responsible for installing and removing all connections to existing systems and shall ensure work and materials are in accordance with local codes.  The use of the electricity shall be limited to tools that can be operated on 60 Hertz, single phase, 20 ampere, 120 volt circuits.

3.	TELEPHONE: Telephone services will not be available for use by the Contractor.

4.	WATER HOOKUP: All connections to the water system shall be equipped with back flow protection.  Temporary potable water pipes and hoses shall be sterilized before being placed in operation and every time the system is opened to the atmosphere for repair or relocation.

5.	SANITARY FACILITIES: It shall be the Contractor's responsibility to furnish and maintain approved portable toilet facilities for all Contractor personnel.  The On-Site Representative will designate the physical location for the facility and the Contractor shall maintain the toilet facility to the satisfaction of the Government.  Contractor personnel are forbidden to use toilet facilities within existing buildings.

SECTION 01 51 13

EQUIPMENT/UTILITY LOCKOUT AND TAGOUT REQUIREMENTS

1.	GENERAL:  The Contractor shall comply with OSHA 29 CFR 1910.147, “The Control of Hazardous Energy” (Lockout/Tagout).  The Contractor shall provide a Lockout/Tagout Plan to the Contracting Officer prior to starting any work affected by the energy in the equipment/utility system.

2.	APPLICATION:  The Contractor shall be responsible for locking out and tagging out of service, all equipment/utility systems involved in the work under this contract.  After the Contracting Officer’s Representative has approved an outage, Government personnel and the Contractor shall independently secure the equipment/utility system and tag the respective system out of service.  The Contractor shall provide their own locks and chains that are required to secure the equipment/utility systems; e.g., steam, water, air, and/or electricity.

SECTION 01 51 16

TEMPORARY FIRE PROTECTION

1.	Temporary Fire Protection:  Install and maintain temporary fire-protection facilities to protect against predictable and controllable fire loss.  Comply with NFPA 10 "Standard for Portable Fire Extinguishers" and NFPA 241 "Standard for Safeguarding Construction, Alterations and Demolition Operations".

1.1	Locate fire extinguishers where convenient and effective for their intended purpose, but not less than one extinguisher at each floor stairwell and one at each building construction opening for personnel egress.

1.2	Maintain unobstructed access to fire extinguishers, fire hydrants, temporary fire-protection facilities, stairways and other access routes for fighting fires.

1.3	Provide independent supervision of welding, flame cutting and other open flame work.  Provide each fire supervisor with an appropriate fire extinguisher.

1.4	Provide training for all personnel on-site in the proper operation of each type of fire extinguisher provided.  Provide all personnel with the proper notification procedure to summon the local fire department or emergency medical service.

1.5	There shall be NO SMOKING or unsupervised open flame permitted inside any structure, temporary or permanent; nor within 25 feet of combustible material or within 50 feet of flammable liquids or compressed gasses.

SECTION 01 54 30

CONFINED ENTRY

1.	COMPLIANCE:  The Contractor shall comply with OSHA 29 CFR 1910.146, Permit-Required Confined Space.  The Contractor shall provide a Confined Space Entry Plan to the Contracting Officer prior to entering, or starting any work, in a confined space.  The Contractor shall provide all equipment and materials as required to comply with OSHA and complete the work under this contract.

SECTION 01 55 00

ACCESS ROADS AND PARKING

1.	ACCESS:  Access to the site is available from public roads.  Any damage to these roads by the Contractor's vehicles shall be repaired without cost to the Government.

2.	PARKING:  Vehicular operations and parking shall comply with all applicable government orders and regulations.  All driveways and entrances serving the Government shall be kept clear and available to emergency vehicles at all times.

3.	VEHICLE AND VEHICLE OPERATION:  All vehicles, owned by the Contractor or employees of the Contractor, and operators of these vehicles, shall meet all state regulations for safety, noise, loading and minimum liability insurance.  All vehicle operators demonstrating reckless or careless operation in the opinion of the Government shall not be allowed to operate vehicles on government property for the duration of the contract.

4.	VISITORS:  No visiting vehicles will be permitted on government property unless the operator is employed by a subcontractor or supplier.

SECTION 01 55 29

STAGING AREAS AND ACCESS

1.	LOCATION:  The Contractor shall store materials and operate equipment within the confines of the staging area identified by the Government.  Storage of materials outside of the staging area will not be permitted.

2.	COORDINATION:  Two weeks prior to construction, the Contractor shall contact MK1 Joel Gibney, Engineer Petty Officer, U.S. Coast Guard Station Oregon Inlet at (252) 441-6260 or joel.m.gibney@uscg.mil to verify the condition of the staging area.

3.	ADJACENT AREAS:  The Contractor shall ensure that all land and vegetation adjacent to the staging area and access drive remain undisturbed and undamaged; all damages shall be repaired at no cost to the Government.

SECTION 01 56 00

LIGHTS, SIGNS & BARRICADES

1.	GENERAL:  The contractor shall provide and maintain all warning lights, sign, and barriers to insure the safety of pedestrians or vehicles traveling near or through any hazardous area caused by the execution of the Contract work.

2.	LIGHTING:  All lighting requirements shall meet table 7-1 in the US Army Corps of Engineers Safety and Health Requirements Manual (EM 385-1-1).

3.	BARRICADES:  Hard barricades or flexible barriers shall completely encompass all exterior work areas.  Flexible barriers shall consist of 1/2 inch steel bars or 2" X 2" wood stakes driven 12 inches minimum into hard packed soil.  Space stakes on a maximum 10 feet interval and with two rows of yellow or orange 1/4 inch diameter rope (wire and plastic tape are not acceptable) at 24 inches and 36 inches each above ground.

4.	HAZARD FENCING:  Special fencing 4 foot high shall be installed to prevent small children or pets from entering the work area when within 300 feet of family housing or for special hazards as shown on the drawings.

SECTION 01 57 13

EROSION AND SEDIMENT CONTROL

1.	GENERAL:  The Contractor shall plan and execute all earthwork to minimize the duration of exposure of unprotected soils.  Temporary protection shall be provided on side and back slopes as soon as rough grading is completed or when sufficient soil is exposed to require protection to prevent erosion.  All earthwork brought to final grade shall be finished immediately.

2.	METHODS:  The Contractor shall prevent erosion, control sedimentation, and prevent waterborne soil from entering surface waters, ditches, and storm drain inlets by use of any or all of the following methods.

2.1	Mechanical Control:  Divert runoff by constructing ditches or berms.  Filter runoff using straw bale dikes, filter fabric dams or other methods.

2.2	Sediment Basins:  Trap sediment in temporary basins sized to accommodate the runoff of a local 25-year storm.  Pump basins dry and remove accumulated sediment after each storm.  Use a paved weir or vertical overflow pipe for overflow.  Establish effluent quality monitoring programs as required by federal, state, and local regulations.

2.3	Vegetation and Mulch:  Protect slopes by accelerated growth of vegetation, mulching, or netting.  Stabilize slopes by hydroseeding, sodding, anchoring mulch or netting in place.

2.4	Geotextiles:  Protect and stabilize slopes by anchoring geotextile fabric or matting.  The Contractor shall use a geotextile designed and sized for the particular application.

3.	OTHER METHODS:  Other erosion and sediment control methods may be used, as authorized by the Contracting Officer.

SECTION 01 57 23

POLLUTION CONTROL

1.	Volatile Organic Compound (VOC) Regulations:  Contractors are required to comply with local, state and federal VOC compliance laws and regulations in the foregoing order of precedence.  In order to comply with the provisions of the Clean Air Act, each state must have a State Implementation Plan.  Some contractors may be required to abide by the provisions of a Title V Permit.  Some contractors may be required by state or local law to operate under the terms of a Compliance Plan to reduce VOC Emissions.

1.1	In accordance with the Notice to Proceed Letter, the contractor will submit copies of any local, state or federal implementation plans, permits or compliance plans required/applicable to the use/application of VOCs at contractor's facility or offsite work places.

1.2	If no local, state or federal implementation plans, permits or compliance plans are required/applicable to the use/application of VOCs, then the contractor shall submit to the designated Contracting Officer a letter, notarized under oath, that such documents are not required.

1.3	If the use of paint is required the contractor shall submit to the Contracting Officer and in accordance with the Notice to Proceed Letter, certificates, specifications or manufacturing data verifying the VOC rating.

2.	SPILL RESPONSE PLAN:  The Contractor shall submit a Spill Response Plan covering all regulated materials brought to the site for execution of work and all wastes generated as a result of the work to the Contracting Officer.  The plan shall include, at a minimum, the following:  types and quantity of all substances covered under this plan; the reportable quantity (RQ) for each substance; the on-site storage location of each substance; the Contractor's spill response equipment, if applicable; procedures to be followed for responding to a spill, including initial responses to be taken; procedures to be followed in reporting a spill, including the names and telephone numbers for all federal, state, and local agencies/authorities to be notified; and the name, address, and telephone number (work, home, cell and pager) of all Contractor response and media relations personnel.

2.1	In the event of a spill or release, the Contractor shall be responsible for immediate implementation of the spill response plan and restoration of the site to pre-spill condition at no cost to the Government.  The Contractor shall also immediately notify the Contracting Officer to coordinate further notifications.

SECTION 01 65 00

RECOVERED MATERIALS NOTICE

1.	GENERAL:  It is the intent of CEU Cleveland to comply with the requirements of Section 6002 of the Solid Waste Disposal Act as amended by the Resource Conservation and Recovery Act (RCRA or the Act) as amended, 42 U.S.C. 6962 and Executive Order 12873 as they apply to the procurement of the materials designated in paragraph 2.

2.	DESIGNATED RECOVERED MATERIALS:  It is the purpose of this section to designate items that are or can be made with recovered materials.  These designated items can be found at https://www.epa.gov/smm/comprehensive-procurement-guideline-cpg-program#products.

3.	CONTRACTOR RESPONSBILITY:  The contractor should provide recycled materials to the extent practical, provided the materials meet all other requirements of the applicable specification section.

SECTION 01 66 13

HAZARDOUS WASTE

1.	GENERAL:  The Contractor shall comply with all federal, state, and local environmental regulations dealing with the generation, management, storage, and disposal of solid, toxic, and hazardous wastes.  The Contractor shall ensure that all wastes are properly containerized, labeled and placarded, managed, tested, stored, documented/manifested, transported and disposed of in accordance with all applicable regulations.

2.	USED ELECTRIC LAMPS:  40 CFR 273 requires that electric lamps, including incandescent, fluorescent, neon and high intensity discharge (mercury vapor, high/low pressure sodium, metal halide) lamps that are no longer of use be recycled or treated as hazardous waste.  The Contractor shall not dispose of any used electric lamps as solid waste.  The Contractor shall recycle all waste electric lamps generated as a result of this work only at a licensed recycling facility.

3.	METALS:  Unless noted otherwise, scrap metal shall not be landfilled or treated as hazardous waste.  Recycle all scrap metal by smelting or any other acceptable recycling process.  Scrap metal includes ductwork, light fixture housings, pipe, mechanical and electrical equipment, doors and frames, etc.

4.	SUBMITTALS:  The Contractor shall provide the Contracting Officer with signed and fully executed originals of all hazardous waste profiles, test results, hazardous waste manifests and/or other shipping papers, electric lamp disposal documents and all other required documentation.  Maximum payment retention shall be withheld until this documentation is received.

SECTION 01 66 16

SAFETY DATA SHEETS AND MATERIAL HANDLING PROCEDURES

1.	DATA SHEETS: Submit a Safety Data Sheet (SDS) for all materials containing hazardous substances required for contract execution. Information provided in SDS’s shall meet the requirements of 29 CFR 1910.1200. SDS’s require Contracting Officer review and acceptance prior to bringing these materials on site.

2.	MATERIAL STORAGE: Limit the quantity of these materials stored on site to the amount needed for execution of work. Storage of excess materials will not be permitted. Assure that the storage of these materials comply with all applicable federal, state, and local laws and regulations and provide additional storage facilities (paint lockers, etc.) as required for the storage of such materials. Coordinate the physical location of storage areas with the On-site Representative prior to bringing these materials on site.

3.	PROTECTIVE MEASURES: The contractor shall take all protective measures outlined on the SDS’s and as required by federal, state, and local regulations to protect all personnel in the vicinity of the work area from exposure to these materials.  The Contractor shall submit a separate plan outlining the measures required.  Include any required protective measures in the Safety Plan (See Section 01 35 29, “Safety Program”).  The Contracting Officer's Representative shall review protective measures prior to allowing use of these materials.

4.	DISPOSAL OF EXCESS MATERIAL: The Contractor shall dispose of all excess hazardous materials as required by the SDS and all applicable federal, state, and local laws and regulations.

SECTION 01 71 33

PROTECTION FROM WEATHER AND CONSTRUCTION OPERATIONS

1.	TEMPORARY ENCLOSURES: Protect existing facilities/equipment and new construction, whether in progress or newly completed, from the adverse effects of the weather and construction operations.  Provide temporary enclosures, coverings and barriers as required to afford protection against exposure, weather and wind damage and from construction operations which could degrade, stain, age, or reduce the finished quality of new work or damage existing facilities and equipment.

2.	REAPPLICATION:  All temporary closures or enclosures shall be made ready for immediate re-application in the event of sudden storms or man-made conditions requiring protection of existing facilities or completed construction.

3.	CLIMATE CONTROL:  Where temporary heat is required during construction to protect work completed or to heat facilities in operation by the Coast Guard, all openings shall be made weather tight to allow the maintenance of 68 degrees F heat minimum with the existing or temporary heating equipment or 78 degrees F. maximum with existing or temporary cooling.

NOTE TO OFFEROR: CLIMATE CONTROL SPECIFICALLY REQUIRED BY THIS CONTRACT WILL BE SPECIFIED IN THE STATEMENT OF WORK AND/OR ASSOCIATED DRAWINGS.

4.	PIPING:  Prevent water-filled pipes or tanks from freezing for both interior and exterior systems installed or in storage.

SECTION 01 74 00

GENERAL CLEANUP & SITE RESTORATION OF WORK AREAS

1.	GENERAL:  The Contractor shall remove and properly dispose of all trash and debris incidental to the contract work from the limits of government property, as well as all adjacent affected areas.  The Contracting Officer shall determine the extent and interval of these cleanups.

2.	WORK AREA CLEANUP:  At the end of each day the entire work area and all adjacent affected areas shall be thoroughly cleaned by removing all trash, debris, dust, etc. caused by the contract work.  Any floor, wall or ceiling surfaces that may have been stained or soiled by the contract work shall be restored to pre-construction condition.

3.	SITE RESTORATION:  If at any time while performing the contract the Contractor causes damage or destruction to any portion of any Government facility or grounds; e.g., bulkheads, pavement, lawns, shrubbery, etc., it shall be the Contractor's responsibility to replace and/or restore the damage as approved by the Contracting Officer’s Representative at no additional cost to the Government.

4.	POST CONSTRUCTION CLEANUP:  Upon completion of the job, the Contractor shall clean up the job site, returning it to a state of cleanliness equal to or exceeding that in which it was found.  The Contractor shall properly dispose of any trash, extra materials, dirt, debris, or other litter that remains.  If the job site appearance is not to the satisfaction of the Contracting Officer’s Representative, final acceptance will not be approved.

SECTION 01 78 00

AS BUILT DRAWINGS

1.	GENERAL:  Maintain one full size set of contract drawings to record variations from the original design.  All deviations shall be neatly and clearly marked in RED on these drawings to show work and/or materials actually provided.  As Built drawings shall be updated as work progresses and kept at the work site for the duration of the contract. These drawings shall be available for Contracting Officer Representative review upon request.

2.	DISCOVERED UTILITIES:  Indicate the exact location of any underground utility lines discovered in the course of the work on the As-Built drawings.

3.	PERMITTED VARIATIONS:  As Built drawings shall reflect the actual construction and materials provided when alternative materials or work methods are allowed in the specifications and/or drawings or if the scope is altered by award of bid items, subsequent changes or modifications.

4.	STANDARDS:  Variations shown on As Built drawings shall be neat, clear and conform with standard drafting practices.  Mark-ups shall include supplementary notes, legends, and details necessary to convey the exact representation of construction actually provided. To comply with Computer Assisted Design (CAD) practices, only full size AS BUILT drawings are acceptable.

5.	SUBMITTAL: Submit As Built drawings for Contracting Officer acceptance upon completion of the contract. Final payment will not be until all required As-Built drawings are accepted. Maximum retention shall be withheld for late or incomplete As Built drawings.

SECTION 01 78 23

OPERATING INSTRUCTIONS AND TRAINING

1.	MANUALS:  Upon completion of the work, but before the work is accepted by the Government, the Contractor must forward two complete bound sets of instructions, tabbed and identified for reference, for all equipment and/or systems provided under this contract. The instructions shall include component parts, manufacturer's certificates, warranty slips, parts lists, descriptive brochures, and manufacturer's maintenance and operating instructions.

2.	TRAINING:  The Contractor shall provide two hours of training, which shall explain to the Government’s personnel all procedures necessary to operate and maintain all equipment and systems on a continuing basis.  A verification of training shall be provided.

SECTION 01 80 00

FACILITY PREVENTATIVE MAINTENANCE PROGRAM (FPMP)

1.	GENERAL:  The intent of this section is for the Contractor to complete the Equipment Enrollment Form (EEF) spreadsheet for systems that have been installed or demolished under this project and are listed in the USCG Approved Equipment Enrollment Catalog.  Both the Approved Equipment Enrollment Catalog and Equipment Enrollment Form  (EEF) are provided as Reference Documents in the solicitation.

At a minimum, the following items require UNIFORMAT II Level 4 designations if the components are used in the contract.

a. Plumbing Systems

b. HVAC Systems

c. Electrical Systems

d. Fire Alarm Systems

e. Fire Suppression Systems

f. Water Systems

g. Compressed Air and Piping Systems

h. Carpet Care, Flooring and Cleaning

i. Battery Systems

j. Any machinery or equipment installed as part of this contract

2.	REFERENCES: The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

ASTM E 1557		Standard Classification for Building Elements and Related Sitework – UNIFORMAT II

3.	SUBMITTALS:  Submit hard copy prints and electronic MS-Excel files of Equipment Enrollment Form (EEF) for Contracting Officer acceptance upon completion of the contract for each Real Property asset that has equipment to be enrolled as part of the FPMP.

### 3.1	Equipment Enrollment Form (EEF) Requirements:

#### 3.1.1	Form Fields:  The following fields are listed on the form and shall be completely filled out except where otherwise noted on the Equipment Enrollment Form.  The actual equipment attribute list below may change slightly prior to the actual start of this enrollment task.

- UNIFORMAT II Level IV Classification

- Component Type (Assigned from Approved Equipment Enrollment Catalog (column D))

- Physical Location, broken down by Floor, and Room #.

- Manufacturer Name

- Model Number

- Serial #

- Installation Date

- Purchase Price (Cost of equipment, labor, shipping)

- Replacement Costs (Cost of equipment only)

- Warranty Expiration Date

- Equipment Attributes (Name Plate information typically indicating Size, Flow, Volume, Pressure, etc.)

#### 3.1.2	Only equipment from a single building and/or structure is allowed per Equipment Enrollment Form (EEF).

#### 3.1.3	Equipment identified for maintenance by O&M manuals but not listed in the Approved Equipment Enrollment Catalog shall also be cataloged per ASTM E 1557 and listed on the equipment enrollment form.  If the equipment is not listed in ASTM E1557, consult the Coast Guard for the proper naming convention.

LIST OF SUBMITTALS

| SECT | PARA | ITEM | key | general use column |
| --- | --- | --- | --- | --- |
| 01 14 14 | 1 | Pre-Con Site Conditions |  |  |
| 01 14 16 | 3.1 | Airfield Interference Schedule |  |  |
| 01 12 16 | 1 | Project Phasing Plan |  |  |
| 01 32 16 | 1.a | Construction Schedule |  |  |
|  | 1.b | Schedule of Values |  |  |
|  | 2.a | Progress Schedule |  |  |
| 01 35 29 | 3 | Safety Plan |  |  |
| 01 51 13 | 1 | Lockout/Tagout Plan |  |  |
| 01 54 30 | 1 | Confined Space Entry Plan |  |  |
| 01 57 23 | 1.1 | State Implementation Documentation |  |  |
|  | 1.2 | Notarized Letter |  |  |
|  | 1.3 | VOC rating documentation |  |  |
|  | 2 | Spill Response Plan |  |  |
| 01 66 13 | 4 | Hazardous Waste Documents |  |  |
| 01 66 16 | 1 | SDS |  |  |
|  | 3 | Protective Measures |  |  |
| 01 78 00 | 5 | As-Built Drawings |  |  |
| 01 78 23 | 1 | Operating Instructions |  |  |
|  | 2 | Verification of Training |  |  |
| 01 80 00 | 3 | Equipment Enrollment Form(s) |  |  |
| 02 41 19 | 1.4 | Existing Conditions |  |  |
|  | 1.4 | Disposal of Ozone Depleting Substances (ODS) |  |  |
|  | 1.4 | Receipts or Bills of Ladings |  |  |
|  | 1.5.1 | Refrigerant Recovery Technician Qualifications |  |  |
|  | 1.5.2 | Demolition |  |  |
| 07 21 16 | 2.2 | Blanket Insulation |  |  |
|  | 2.4 | Pressure Sensitive Tape |  |  |
|  | 2.5 | Accessories |  |  |
| 07 27 36 | 1.3 | Daily Work Record |  |  |
|  | 1.3 | General Site Inspections | X |  |
|  | 1.3 | Manufacturer’s Site Inspections | X |  |
|  | 1.3 | Contractor’s Site Inspections | X |  |
|  | 1.4 | Spray Foam Air Barrier | X |  |
|  | 1.4.1 | Shop Drawings |  |  |
|  | 1.4.2 | Safety Data Sheets |  |  |
|  | 1.4.4 | Field Peel Adhesion Test |  |  |
|  | 1.4.4 | Fire-Ratings of Ignition Barrier Materials |  |  |
|  | 1.4.4 | Flame Spread and Smoke Developed Index Ratings of SPF Products |  |  |
|  | 1.5.1 | SPF Handling, Storage, Spray Procedures |  |  |

| SECT | PARA | ITEM | key | general use column |
| --- | --- | --- | --- | --- |
| 07 27 36 | 1.7.1 | Fire Prevention Plan |  |  |
|  | 1.7.2 | Respirator Plan |  |  |
|  | 1.8.1 | Qualification of Manufacturer |  |  |
|  | 1.8.2 | Qualification of Installer |  |  |
|  | 2.1.1 | Volatile Organic Compound (VOC) Contents |  |  |
|  | 2.2.2.j | Closed Cell | X |  |
|  | 2.2.2.n | Recycled Content |  |  |
| 07 92 00 | 2.1 | Sealants |  |  |
|  | 2.2 | Primers |  |  |
|  | 2.3 | Bond Breakers |  |  |
|  | 2.4 | Backstops |  |  |
| 09 29 00 | 1.3.1 | Indoor Air Quality |  |  |
|  | 2.2 | Material Safety Data Sheets |  |  |
|  | 2.2 | Manufacturer Maintenance Instructions |  |  |
|  | 2.2 | Asbestos Free Materials |  |  |
|  | 2.2.1 | Recycled Content for Gypsum Board |  |  |
|  | 2.2.1 | Indoor Air Quality for Gypsum Board |  |  |
|  | 2.2.1 | Gypsum Board |  |  |
|  | 2.2.5 | Accessories |  |  |
| 09 51 00 | 1.2.4 | Acoustical Ceiling Systems |  |  |
|  | 1.4 | Certifications |  |  |
|  | 1.8 | Warranty |  |  |
| 09 90 00 | 1.3.1 | Certification |  |  |
|  | 1.6 | Safety |  |  |
|  | 1.9 | Color |  |  |
|  | 1.10.3.1 | Qualification Testing |  |  |
|  | 2.1 | Coating |  |  |
|  | 2.1 | Manufacturer’s Technical Data Sheets |  |  |
| 22 00 00 | 1.2 | Tests, Flushing and Disinfection |  |  |
|  | 1.2 | Plumbing System |  |  |
|  | 1.3 | Materials and Equipment |  |  |
|  | 2.4 | Water Heaters |  |  |
| 23 00 00 | 1.2.1.2 | Diagrams | X |  |
|  | 1.2.2 | Air Cooled Condensing Units | X |  |
|  | 1.2.2 | Air Handling Units | X |  |
|  | 1.2.2 | Energy Recovery Ventilator Units | X |  |
|  | 1.3 | Manufacturer’s Installation Instructions |  |  |
|  | 1.3 | Operation and Maintenance Manuals |  |  |
|  | 1.3 | Operation and Maintenance Training |  |  |
|  | 1.4.3 | Ozone Depleting Substances | X |  |
|  | 1.4.3.1 | Proof Of Technician Certification |  |  |

| SECT | PARA | ITEM | key | general use column |
| --- | --- | --- | --- | --- |
| 23 00 00 | 1.4.3.2 | Proof of Equipment Certification For Recovery Or Recycling Equipment |  |  |
|  | 1.4.3.3 | Proof Of Availability of Certified Recovery Or Recycling Equipment |  |  |
|  | 1.4.5 | Detail Drawings |  |  |
|  | 1.4.6 | Test Procedures |  |  |
|  | 2.5 | Bolts |  |  |
|  | 2.8.1 | Diffusers, Registers, and Grilles | X |  |
| 23 03 00 | 1.4.1 | Material and Equipment Qualifications |  |  |
|  | 3.1.1 | Factory Painting Systems Certification |  |  |
| 23 05 93 | 1.2 | Design Review Report | X |  |
|  | 1.2 | TAB Related HVAC Submittals | X |  |
|  | 1.2 | TAB Schematic Drawings and Report Forms |  |  |
|  | 1.2 | TAB Procedures |  |  |
|  | 1.2 | TAB Execution |  |  |
|  | 1.2 | Systems Readiness Check |  |  |
|  | 1.2 | TAB Report | X |  |
|  | 1.4.1 | Site Visit and Design Review |  |  |
|  | 1.7.1 | TAB Firm |  |  |
|  | 1.7.2 | TAB Specialist |  |  |
|  | 2.1 | Calibration |  |  |
| 23 07 00 | 1.3 | Equipment Insulation Systems | X |  |
|  | 2.3 | Pipe Insulation Systems | X |  |
|  | 2.4 | Duct Insulation Systems | X |  |
| 23 09 53 | 1.3 | Existing System Report |  |  |
|  | 1.5.1 | Control System Diagrams | X |  |
|  | 1.5.2 | Ladder Diagram | X |  |
|  | 1.5.3 | Operating Parameters | X |  |
|  | 1.5.4 | Wiring Diagram | X |  |
|  | 1.5.5 | Sequence of Operation | X |  |
|  | 1.6 | Notification of Planned Testing |  |  |
|  | 1.6 | Test Procedure |  |  |
|  | 1.6 | Test Review Meeting |  |  |
|  | 1.6 | Written Report |  |  |
|  | 1.6 | Certification of Completion |  |  |
|  | 1.6 | Performance Verification Test |  |  |
|  | 1.6 | Training |  |  |
|  | 1.6 | Qualified Service Organization List |  |  |
|  | 1.7.4 | Site Testing Procedures | X |  |
|  | 1.7.5 | Commissioning Procedures | X |  |
|  | 1.7.6 | Calibration Adjustment and Commissioning Report | X |  |

| SECT | PARA | ITEM | key | general use column |
| --- | --- | --- | --- | --- |
| 23 09 53 | 1.7.7 | Space Temperature Control System | X |  |
|  | 2.2 | Actuators | X |  |
|  | 2.3 | Thermostats | X |  |
|  | 2.4 | Indicating Devices | X |  |
|  | 2.5 | Controllers | X |  |
| 23 23 00 | 2.2 | Refrigerant Piping System | X |  |
|  | 2.3 | Pipe, Fittings and End Connections (Joints) |  |  |
|  | 2.4 | Valves |  |  |
|  | 2.5 | Piping Accessories |  |  |
|  | 2.5.2 | Pipe Hangers, Inserts, and Supports |  |  |
| 23 81 00 | 1.1.D | Contractor’s Qualifications |  |  |
|  | 1.3 | Manufacturer’s Standard Catalog |  |  |
|  | 1.3 | Outdoor Heat Pump Units |  |  |
|  | 1.3 | Indoor Fan Coil Units |  |  |
|  | 1.3 | Branch Controllers |  |  |
|  | 1.3 | Controls |  |  |
|  | 1.3 | List of Units to be Included I O&M Manuals |  |  |
| 23 81 01 | 1.3 | Start-Up and Initial Operational Tests |  |  |
|  | 1.4.2 | Control System Wiring | X |  |
|  | 1.4.4 | Packaged Air Conditioning Unit | X |  |
|  | 1.5 | Refrigerant | X |  |
|  | 2.1 | Air Conditioners | X |  |
|  | 2.1.8 | Thermostats | X |  |
|  | 2.2 | Filters |  |  |
|  | 2.5.1 | Salt-Spray Tests |  |  |
| 26 00 00 | 1.6 | Warranty |  |  |
|  | 1.7 | Posted Operating Instructions |  |  |
| 26 20 00 | 1.3 | 600-Volt Wiring Test |  |  |
|  | 1.3 | Ground-Fault Receptacle Test |  |  |
|  | 1.3 | Grounding System Test |  |  |
|  | 2.8 | Switches |  |  |
|  | 2.9 | Receptacles |  |  |
|  | 2.10.3 | Circuit Breakers |  |  |
|  | 2.11 | Enclosed Circuit Breakers |  |  |
|  | 2.18 | Surge Protective Devices |  |  |

CONTRACT  ITEM  ACCEPTANCE  REQUEST

| Contract Number: HSCG83- | DO/TO: HSCG83- |
| --- | --- |
| Contract Specialist: | Project Number: |
| Contractor Name: |  |

URGENT     YES      NO                       (if yes)  CONTRACTOR FAX #: _______________________

Submittal #_____________________	Job Location:  ___________________________________

NOTE:  Contractor must mark Deviation column if submittal deviates from contract requirements

| Item No. | Spec Section and Paragraph | Description of Material Include Type, Model #, Manufacturer, Etc. | Deviation | Status |
| --- | --- | --- | --- | --- |

STATUS ABBREVIATION GUIDE:

AC - Accepted

AC w/ CMT - Accepted with Comment

R-Resubmit

Comments:

| Typed Name & Title | Signature | Date |
| --- | --- | --- |

NOTE:  Review and acceptance of submittals by the Government is intended to verify general conformance with the design intent as shown on the contract drawings and in the specifications.   Acceptance by the Contracting Officer’s Representative does not relieve the Contractor of responsibility for any errors and/or omissions in the submittals, nor from the responsibility for complying with the requirements of the contract, except with respect to variations described and approved in accordance with FAR 52.243-4 CHANGE

SECTION 02 41 19

DEMOLITION AND REMOVAL

# PART 1   GENERAL

## 1.1   GENERAL

Work Included: Furnish all labor, materials, and equipment necessary to demolish and remove from the site all items noted on the drawings and as required to accomplish the contract work.

## 1.2   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 241	(2013) Standard for Safeguarding Construction, Alteration, and Demolition Operations

## 1.3   DEFINITIONS

### 1.3.1   Remove:

Detach items from existing construction and legally dispose of them off-site, unless indicated to be removed and salvaged or removed and reinstalled.

### 1.3.2   Remove and Reinstall

Detach items from existing construction, prepare them for reuse, and reinstall them where indicated.

### 1.3.3   Existing to Remain

Existing items of construction that are not to be removed and that are not otherwise indicated to be removed, removed and salvaged, or removed and reinstalled.

## 1.4   SUBMITTALS

Contracting Officer’s written approval is required for submittals.  Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-01 Preconstruction Submittals

Existing Conditions

Existing conditions submittal shall include pre-demolition Photographs or Videos: Show existing conditions of adjoining construction and site improvements, including finish surfaces that might be misconstrued as damage caused selective demolition operations.

Demolition Plan

The demolition plan shall indicate equipment to be used for demolition and proposed sequence of operations for review prior to start of new work.  The demolition plan shall also include detailed sequence of demolition and removal work with starting and ending dates/times for each activity, to ensure uninterrupted progress of Coast Guard's on site operations.  The plan shall include locations of proposed dust- and noise-control temporary partitions and means of egress.  The plan shall include the coordination of USCG continuing occupancy of portions of existing building, and of USCG partial occupancy of completed Work.

SD-07 Certificates

Qualifications Data

Refrigerant Recovery Technician Qualifications: Certified by an EPA-approved certification program.

Receipts Or Bills Of Lading

Disposal Of Ozone Depleting Substances (ODS)

## 1.5   QUALITY ASSURANCE

### 1.5.1   Refrigerant Recovery Technician Qualifications:

Certified by an EPA approved certification program.

### 1.5.2   Regulatory Requirements:

Comply with governing EPA notification regulations before beginning selective demolition.  Comply with hauling and disposal regulations of authorities having jurisdiction.

### 1.5.3   Standards:

Comply with ANSI A10.6 and NFPA 241.

## 1.6   SAFETY REQUIREMENTS

Comply with federal, state and local hauling and disposal regulations.  In addition to the requirements of the "Contract Clauses", safety requirements shall conform to ANSI A10.6.  It is the responsibility of the Contractor to be aware of and comply with all pertinent environmental regulations. The contractor shall properly dispose of all wastes generated during the execution of this work.

## 1.7   PROJECT CONDITIONS

### 1.7.1   Occupancy

Owner shall occupy portions of building immediately adjacent to selective demolition area. Conduct selective demolition so Coast Guard operations will not be disrupted.

### 1.7.2   Removed Items:

Storage or sale of removed items or materials on-site is not permitted.

## 1.8   PROTECTION

### 1.8.1   Existing Work and Utilities:

Conduct work and provide protection so not to damage existing work and utilities which are to remain in place, be reused, be relocated, or remain the property of the Government.  Such items damaged shall be restored to their original condition or replaced with new. Do not overload structures or structural elements.  Provide new supports and reinforcement for existing construction weakened by demolition or removal work. Repairs, reinforcement, or structural replacement must have COR approval.  The Contractor is financially responsible for damage to existing work and utilities.

### 1.8.2   Hazardous Materials:

It is not expected that hazardous materials will be encountered in the Work.  If materials suspected of containing hazardous materials are encountered, do not disturb; immediately notify the Contracting Officer.  Comply with applicable regulations, laws, and ordinances concerning removal, handling, and protection against exposure and environmental pollution.

# PART 2   PRODUCTS

Not used.

# PART 3   EXECUTION

## 3.1   EXAMINATION

Examination:  Verify that utilities have been disconnected and capped. Survey existing conditions and correlate with requirements indicated to determine extent of selective demolition required.  Inventory and record the condition of items to be removed and reinstalled and items to be removed and salvaged.  When unanticipated mechanical, electrical, or structural elements that conflict with intended function or design are encountered, investigate and measure the nature and extent of conflict.  Promptly submit a written report to COR and Contracting Officer.  Perform surveys as the Work progresses to detect hazards resulting from selective demolition activities.  Record existing conditions by use of pre-construction photographs.

## 3.2   UTILITY SERVICES AND MECHANICAL/ELECTRICAL SYSTEMS

### 3.2.1   Existing Services/Systems

Maintain services/systems indicated to remain and protect them against damage during selective demolition operations.

### 3.2.2   Service/System Requirements

Locate, identify, disconnect, and seal or cap off indicated utility services and mechanical/electrical systems serving areas to be selectively demolished.  If services/systems are required to be removed, relocated, or abandoned, before proceeding with selective demolition provide temporary services/systems that bypass area of selective demolition and that maintain continuity of services/systems to other parts of building.  Cut off pipe or conduit in walls or partitions to be removed.  Cap, valve, or plug and seal remaining portion of pipe or conduit after bypassing.  Where entire wall is to be removed, existing services/systems may be removed with removal of the wall.

## 3.3   PREPARATION

Site Access and Temporary Controls:  Conduct selective demolition and debris-removal operations to ensure minimum interference with roads, streets, walks, walkways, and other adjacent occupied and used facilities.

## 3.4   SELECTIVE DEMOLITION

Demolish and remove existing construction only to the extent required by new construction and as indicated.  Protect construction indicated to remain against damage and soiling during selective demolition.  Use methods required to complete the Work within limitations of governing regulations and as follows:

### 3.4.1   Openings

Neatly cut openings and holes plumb, square, and true to dimensions required.  Use cutting methods least likely to damage construction to remain or adjoining construction.  Use hand tools or small power tools designed for sawing or grinding, not hammering and chopping, to minimize disturbance of adjacent surfaces.  Temporarily cover openings to remain.

### 3.4.2   Finished Surfaces

Cut or drill from the exposed or finished side into concealed surfaces to avoid marring existing finished surfaces.

### 3.4.3   Torches

Do not use cutting torches until work area is cleared of flammable materials.  At concealed spaces, such as duct and pipe interiors, verify condition and contents of hidden space before starting flame-cutting operations.  Maintain fire watch and portable fire-suppression devices during flame-cutting operations.  Maintain adequate ventilation when using cutting torches.

### 3.4.4   Dangerous or Unsuitable Materials

Remove decayed, vermin-infested, or otherwise dangerous or unsuitable materials and promptly dispose of off-site.

### 3.4.5   Excessive Loads

Locate selective demolition equipment and remove debris and materials so as not to impose excessive loads on supporting walls, floors, or framing.

### 3.4.6   Demolished Items

Dispose of demolished items and materials promptly.

### 3.4.7   Masonry

Demolish in small sections.  Cut masonry at junctures with construction to remain, using power driven saw then remove masonry between saw cuts.

## 3.5   TITLE TO MATERIALS

Except where specified in other sections, all materials and equipment removed and not to be salvaged, shall become the property of the Contractor and shall be removed from Government Property.  Title to materials resulting from demolition, and materials and equipment to be removed, is vested in the Contractor upon removal from the site after approval by the Contracting Officer of the Contractor's demolition and removal procedures.  The Government will not be responsible for the condition or loss of, or damage to, such property after notice to proceed.  Materials and equipment shall not be viewed by prospective purchasers or sold on the site.

## 3.6   CLEANUP

Remove tools, equipment, and demolished materials from the site. Remove protections, barricades and temporary work.  Clean adjacent structures and improvements of dust, dirt, and debris caused by selective demolition operations.  Return adjacent areas to condition existing before selective demolition operations began.

## 3.7   DISPOSAL OF DEMOLISHED MATERIALS

### 3.7.1   General

Except for items or materials indicated to be recycled, reclaimed, reused, salvaged, reinstalled, or otherwise indicated to remain Owner's property; remove demolished materials from Project site and legally dispose of them in an EPA-approved landfill.  Do not allow demolished materials to accumulate on-site.  Remove and transport debris in a manner that will prevent spillage on adjacent surfaces and areas.

### 3.7.2   Burning

Do not burn demolished materials.

### 3.7.3   Disposal

Transport demolished materials off the Coast Guard property and legally dispose of them.

### 3.7.4   Disposal of Ozone Depleting Substances (ODS)

Disposal of Ozone Depleting Substance (ODS). R-22 (HCFC-22) is presumed as contained within equipment slated for demolition/removal at this site.  Contractor to field verify order of magnitude.  Contractor is responsible for recovery quantity.

#### 3.7.4.1   Remove and capture all Class ODS refrigerants

Remove and capture all Class ODS refrigerants in accordance with the Clean Air Act Amendment of 1990, and turn in to the Navy by shipping the refrigerant container to the Defense Logistics Agency (DLA) at the following address:

Defense Depot Richmond VA (DDRV)

SW0400 Cylinder Operations

8000 Jefferson Davis Highway

Richmond, VA 23297-5900

#### 3.7.4.2   Prevent discharge of Class I and Class II ODS

Prevent discharge of Class I and Class II ODS to the atmosphere.  Place recovered ODS in cylinders meeting AHRI Guideline K suitable for the type ODS (filled to no more than 80 percent capacity) and provide appropriate labeling.  Recovered ODS shall be removed from Government property and disposed of in accordance with 40 CFR 82.  Submit Receipts or bills of lading, as specified.  Submit a shipping receipt or bill of lading for all containers of ozone depleting substance (ODS) shipped to the Defense Depot, Richmond, Virginia.

#### 3.7.4.3   Special Instructions:

Special Instructions:  No more than one type of ODS is permitted in each container.  A warning/hazardous label shall be applied to the containers in accordance with Department of Transportation regulations.  All cylinders including but not limited to fire extinguishers, spheres, or canisters containing an ODS shall have a tag with the following information:

a.  Activity name and unit identification code

b.  Activity point of contact and phone number

c.  Type of ODS and pounds of ODS contained

d.  Date of shipment

e.  Naval stock number (for information, call (804) 279-4525).

#### 3.7.4.4   Transportation Guidance:

Transportation Guidance: Ship all ODS containers in accordance with MIL-STD-129, DLA 4145.25, 49 CFR 173.301, and DOD 4000.25-1-M. DLA contact information: 804.279.3835, and/or http://www.aviation.dla.mil/UserWeb/aviationengineering/ozone/.

### 3.7.5   Disposal of other refrigerants: Class I and Class II ODS

Disposal of other refrigerants: Class I and Class II ODS are defined in Section, 602(a) and (b), of The Clean Air Act. Dispose of all ODS in accordance with paragraph 3.7.4, whether indicated or not in contract documents.

#### 3.7.5.1   Dispose of all other refrigerants

Dispose of all other refrigerants in accordance with local, State, and Federal laws.

-- End of Section –

SECTION 07 21 16

MINERAL FIBER BLANKET INSULATION

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

ASTM INTERNATIONAL (ASTM)

ASTM C665	(2012) Mineral-Fiber Blanket Thermal Insulation for Light Frame Construction and Manufactured Housing

ASTM C930	(2012) Potential Health and Safety Concerns Associated with Thermal Insulation Materials and Accessories

ASTM D3833/D3833M	(1996; R 2011) Water Vapor Transmission of Pressure-Sensitive Tapes

ASTM E136	(2016) Behavior of Materials in a Vertical Tube Furnace at 750 Degrees C

ASTM E84	(2015b) Standard Test Method for Surface Burning Characteristics of Building Materials

U.S. NATIONAL ARCHIVES AND RECORDS ADMINISTRATION (NARA)

29 CFR 1910.134	Respiratory Protection

## 1.2   SUBMITTALS

Contracting Officer’s written approval is required for submittals.  Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-03 Product Data

Blanket Insulation

Pressure Sensitive Tape

Accessories

## 1.3   DELIVERY, STORAGE, AND HANDLING

### 1.3.1   Delivery

Deliver materials to site in original sealed wrapping bearing manufacturer's name and brand designation, specification number, type, grade, R-value, and class.  Store and handle to protect from damage.  Do not allow insulation materials to become wet, soiled, crushed, or covered with ice or snow.  Comply with manufacturer's recommendations for handling, storing, and protecting of materials before and during installation.

### 1.3.2   Storage

Inspect materials delivered to the site for damage; unload and store out of weather in manufacturer's original packaging.  Store only in dry locations, not subject to open flames or sparks, and easily accessible for inspection and handling.

## 1.4   SAFETY PRECAUTIONS

### 1.4.1   Respirators

Provide installers with dust/mist respirators, training in their use, and protective clothing, all approved by National Institute for Occupational Safety and Health (NIOSH)/Mine Safety and Health Administration (MSHA) in accordance with 29 CFR 1910.134.

### 1.4.2   Other Safety Concerns

Consider other safety concerns and measures as outlined in ASTM C930.

# PART 2   PRODUCTS

## 2.1   PRODUCT SUSTAINABILITY CRITERIA

For products in this section, where applicable and to extent allowed by performance criteria, provide and document the following:

## 2.2   BLANKET INSULATION

ASTM C665, Type II, blankets with non-reflecting coverings; Class A, membrane-faced surface with a flame spread of 25 or less and a smoke developed rating of 150 or less when tested in accordance with ASTM E84.

### 2.2.1   Thermal Resistance Value (R-VALUE)

Minimum (as indicated).

### 2.2.2   Recycled Materials

Provide Thermal Insulation containing recycled materials to the extent practicable, provided the material meets all other requirements of this section.  The minimum required recycled materials content by weight are:

Fiberglass:  20 to 25 percent glass cullet

### 2.2.3   Prohibited Materials

Do not provide asbestos-containing materials.

## 2.3   BLOCKING

Wood, metal, unfaced mineral fiber blankets in accordance with ASTM C665, Type I, or other approved materials.  Use only non-combustible materials meeting the requirements of ASTM E136 for blocking around chimneys and heat producing devices.

## 2.4   PRESSURE SENSITIVE TAPE

As recommended by the vapor retarder manufacturer and having a water vapor permeance rating of one perm or less when tested in accordance with ASTM D3833/D3833M.

## 2.5   ACCESSORIES

### 2.5.1   Adhesive

As recommended by the insulation manufacturer.

### 2.5.2   Mechanical Fasteners

Corrosion resistant fasteners as recommended by the insulation manufacturer.

# PART 3   EXECUTION

## 3.1   EXISTING CONDITIONS

Before installing insulation, ensure that areas that will be in contact with the insulation are dry and free of projections which could cause voids, compressed insulation, or punctured vapor retarders.  If moisture or other conditions are found that do not allow the workmanlike installation of the insulation, do not proceed but notify Contracting Officer and COR of such conditions.

## 3.2   INSTALLATION

### 3.2.1   Insulation

Install and handle insulation in accordance with manufacturer's instructions.  Keep material dry and free of extraneous materials.  Any materials that show visual evidence of biological growth due to presence of moisture must not be installed on the building project.  Ensure personal protective clothing and respiratory equipment is used as required.  Observe safe work practices.

#### 3.2.1.1   Electrical wiring

Do not install insulation in a manner that would sandwich electrical wiring between two layers of insulation.

#### 3.2.1.2   Continuity of Insulation

Install blanket insulation to butt tightly against adjoining blankets and to studs, rafters, joists, sill plates, headers and any obstructions.  Provide continuity and integrity of insulation at corners, wall to ceiling joints, roof, and floor.  Avoid creating thermal bridges.

#### 3.2.1.3   Installation at Bridging and Cross Bracing

Insulate at bridging and cross bracing by splitting blanket vertically at center and packing one half into each opening.  Butt insulation at bridging and cross bracing; fill in bridged area with loose or scrap insulation.

#### 3.2.1.4   Insulation Blanket with Affixed Vapor Retarder

Locate vapor retarder as indicated.  Do not install blankets with affixed vapor retarders unless so specified.  Unless the insulation manufacturer's instructions specifically recommend not to staple the flanges of the vapor retarder facing, staple flanges of vapor retarder at 6 inch intervals flush with face or set in the side of truss, joist, or stud.  Avoid gaps and bulges in insulation and "fishmouth" in vapor retarders.  Overlap both flanges when using face method.  Seal joints and edges of vapor retarder with pressure sensitive tape.  Stuff pieces of insulation into small cracks between trusses, joists, studs and other framing, such as at attic access doors, door and window heads, jambs, and sills, band joists, and headers.  Cover these insulated cracks with vapor retarder material and tape all joints with pressure sensitive tape to provide air and vapor tightness.

#### 3.2.1.5   Sizing of Blankets

Provide only full width blankets when insulating between trusses, joists, or studs.  Size width of blankets for a snug fit where trusses, joists or studs are irregularly spaced.

-- End of Section --

SECTION 07 27 36

SPRAY FOAM AIR BARRIERS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AIR BARRIER ASSOCIATION OF AMERICA (ABAA)

ABAA Accreditation	Accreditation

ABAA QAP	Quality Assurance Program

AMERICAN SOCIETY OF SAFETY ENGINEERS (ASSE/SAFE)

ASSE/SAFE Z88.2	(2015) American National Standard Practices for Respiratory Protection

ASSE/SAFE Z9.2	(2012) Fundamentals Governing the Design and Operation of Local Exhaust Ventilation Systems

ASTM INTERNATIONAL (ASTM)

ASTM C1029	(2015) Standard Specification for Spray-Applied Rigid Cellular Polyurethane Thermal Insulation

ASTM C1303/C1303M	(2015) Standard Test Method for Predicting Long-Term Thermal Resistance of Closed-Cell Foam Insulation

ASTM C1338	(2014) Standard Test Method for Determining Fungi Resistance of Insulation Materials and Facings

ASTM C518	(2015) Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus

ASTM D1621	(2016) Standard Test Method for Compressive Properties of Rigid Cellular Plastics

ASTM D1622	(2014) Apparent Density of Rigid Cellular Plastics

ASTM D1623	(2009) Tensile and Tensile Adhesion Properties of Rigid Cellular Plastics

ASTM D2126	(2009) Response of Rigid Cellular Plastics to Thermal and Humid Aging

ASTM D2842	(2012) Water Absorption of Rigid Cellular Plastics

ASTM D4541	(2009; E 2010) Pull-Off Strength of Coatings Using Portable Adhesion Testers

ASTM D6226	(2010) Standard Test Method for Open Cell Content of Rigid Cellular Plastics

ASTM E2178	(2013) Standard Test Method for Air Permeance of Building Materials

ASTM E2357	(2011) Standard Test Method for Determining Air Leakage of Air Barrier Assemblies

ASTM E283	(2004; R 2012) Determining the Rate of Air Leakage Through Exterior Windows, Curtain Walls, and Doors Under Specified Pressure Differences Across the Specimen

ASTM E736	(2000; R 2011) Cohesion/Adhesion of Sprayed Fire-Resistive Materials Applied to Structural Members

ASTM E84	(2016) Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM E96/E96M	(2016) Standard Test Methods for Water Vapor Transmission of Materials

ICC EVALUATION SERVICE, INC. (ICC-ES)

ICC-ES AC377	(2009) Acceptance Criteria for Spray-Applied Foam Plastic Insulation

INTERNATIONAL CODE COUNCIL (ICC)

ICC IBC	(2015) International Building Code

ICC IECC	(2015) International Energy Conservation Code

INTERNATIONAL SAFETY EQUIPMENT ASSOCIATION (ISEA)

ANSI/ISEA Z87.1	(2015) Occupational and Educational Personal Eye and Face Protection Devices

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 10	(2013) Standard for Portable Fire Extinguishers

NFPA 275	(2017) Standard Method of Fire Tests for the Evaluation of Thermal Barriers

NFPA 285	(2012) Standard Fire Test Method for Evaluation of Fire Propagation Characteristics of Exterior Non-Load-Bearing Wall Assemblies Containing Combustible Components

SPRAY POLYURETHANE FOAM ALLIANCE (SPFA)

SPFA TechDocs	(2015) SPFA Technical Documents Library, four categories:  General, Insulation, Roofing, Specialty

U.S. DEPARTMENT OF DEFENSE (DOD)

UFC 3-600-01	(2016; with Change 1) Fire Protection Engineering for Facilities

U.S. NATIONAL ARCHIVES AND RECORDS ADMINISTRATION (NARA)

29 CFR 1910.132	Personal Protective Equipment

29 CFR 1910.133	Eye and Face Protection

29 CFR 1910.134	Respiratory Protection

## 1.2   DEFINITIONS

### 1.2.1   Long Term Thermal Resistance (LTTR)

The thermal resistance value of a closed cell foam insulation product measured using accelerated aging ASTM C1303/C1303M equivalent to the time-weighted average thermal resistance value over 15 years.  Loss in thermal resistance is attributable to changes in cell gas composition caused by diffusion of air into and blowing agent out of the foam cells.

### 1.2.2   SPFA TechDocs

Reformatted documents, named SPFA TechDocs (http://www.sprayfoam.org/technical/spfa-technical-documents), places each document in one of four categories for easy reference and identification: Roofing, Insulation, Specialty and General.

Spray Polyurethane Foam:  Thermal and air/vapor barrier system consisting of sprayed polyurethane foam (SPF).

## 1.3   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-01 Preconstruction Submittals

Qualification of Manufacturer

Qualification of Installer

Quality Control Plan

Safety Plan

Fire Prevention Plan

Respirator Plan

SD-02 Shop Drawings

Shop Drawings

Spray Foam Air Barrier System

SD-03 Product Data

Closed Cell SPF

Safety Data Sheets

SD-04 Samples

Spray Foam Air Barrier Mockup

SD-06 Test Reports

Field Peel Adhesion Test

Fire-Ratings Of Ignition Barrier Materials

Flame Spread And Smoke Developed Index Ratings Of SPF Products

General Site Inspections Reports

Manufacturer’s Site Inspections Reports

Contractor’s Site Inspections Reports

SD-07 Certificates

Closed cell SPF

Qualification of Manufacturer

Qualification of Installer

SD-08 Manufacturer's Instructions

SPF Handling, Storage, and Spray Procedures

SD-09 Manufacturer's Field Reports

Daily Work Record

SD-11 Closeout Submittals

Volatile Organic Compound (VOC) Content

Recycled Content

## 1.4   MISCELLANEOUS REQUIREMENTS

For the spray foam air barrier system provide the following:

### 1.4.1   Shop Drawings

Submit spray foam air barrier shop drawings showing locations, detailing, and extent of spray foam air barrier assemblies.  Provide details of all typical conditions, intersections with other envelope assemblies and materials.  Provide details for ignition barriers.  Show details for bridging of gaps in construction, treatment of inside and outside corners, expansion joints, methods of attachment of materials covering the SPF without compromising the barrier.  Indicate how miscellaneous penetrations such as conduit, pipes, electric boxes, and similar items will be sealed.

### 1.4.2   Product Data

Submit manufacturer's technical data indicating compliance with performance and environmental requirements, manufacturer's printed instructions for evaluating, preparing, and treating substrates, temperature and other limitations of installation conditions, safety requirements for installation, and Safety Data Sheets.  Indicate flame and smoke spread ratings for all products.  Submit ignition barrier literature including material description, physical properties, and fire-ratings.

### 1.4.3   Mockup

Provide a mockup of each foam system specified. Apply foam in an area designated by the Contracting Officer’s Representative.  Apply an area of not less than 50 square feet. Include all components specified for the finished assembly including primers, support components, expansion and contraction joints, ignition barriers, and other accessories as representative of the complete system.  Isolate the area and protect workers as required by 29 CFR 1910.132, 29 CFR 1910.133 and 29 CFR 1910.134.  Notify the Contracting Officer a minimum of 48 hours prior to the test application.  Select a test area representative of conditions to be sprayed.

### 1.4.4   Test Reports

Submit test reports indicating that field peel adhesion tests on all materials have been performed and the changes made, if required, in order to achieve successful and lasting adhesion.  Submit test reports for flame spread and smoke developed index ratings of SPF products tested in accordance with ASTM E84.  Submit test reports for flame propagation of wall assemblies tested in accordance with NFPA 285.  Submit test reports for fire-ratings of ignition barrier materials tested in accordance with ASTM E84.

## 1.5   DELIVERY, STORAGE, AND HANDLING

### 1.5.1   Delivery

Deliver and store materials in sufficient quantity to allow for uninterrupted flow of work.  Inspect materials delivered to the site for damage; unload and store out of weather.  Deliver materials to the jobsite in their original unopened packages, clearly marked with the manufacturer's name, brand designation, description of contents, and shelf life of containerized materials.  Store and handle to protect from damage.  Submit SPF Handling, Storage, and Spray Procedures in accordance with submittal procedures.

### 1.5.2   Storage

Store materials in clean, dry areas, away from excessive heat, sparks, and open flame.  Maintain temperatures in the storage area below the materials' flash point(s) and within limits recommended by the manufacturer's printed instructions.  Provide ventilation in accordance with ASSE/SAFE Z9.2 to prevent build-up of flammable gases.  Store MDI (A-side) drums in locations that limit the risk of contact with water, acids, caustics (such as lye), alcohols, and strong oxidizing and reducing agents.

### 1.5.3   Handling

Handle materials and containers safely and in accordance with manufacturer's recommendations.  Store liquids in airtight containers and keep containers closed except when removing materials.  Do not use equipment or containers containing remains of dissimilar materials.  Do not expose foam component containers to direct sunlight.  Do not use materials from containers with content temperatures in excess of 80 degrees F.

Containers exposed to long periods of cold may also exhibit separation and poor performance.  Do not use materials exposed to temperature ranges outside of manufacturer's instructions for exposure limits.

Mark and remove from job site materials which have been exposed to moisture, that exceed shelf life limits, or that have been exposed to temperature extremes.

#### 1.5.3.1   Venting and Handling of Material Containers

Partially unscrew material container and drum caps to gradually vent the containers prior to opening.  Do not inhale vapors.  Decontaminate empty component containers by filling with water and allowing to stand for 48 hours with bung caps removed.  Do not, under any circumstances seal, stop, or close containers which have been emptied of foam components.

## 1.6   FIELD PEEL ADHESION TEST

Perform a field peel adhesion test on the construction mockup.  Test the SPF for adhesion in accordance with ASTM D4541 using a Type II pull tester except use a disk that is 4 inches in diameter and cut through the membrane to separate the material attached to the dish from the surrounding material.  Perform test after curing period in accordance with manufacturer's written recommendations.  Record mode of failure and area which failed in accordance with ASTM D4541.  Compare adhesion values with the manufacturer's established minimum values for the particular combination of material and substrate.  Indicate on the inspection report whether the manufacturer's requirement has been met.  Where the manufacturer has not declared a minimum adhesion value for their product and substrate combination, the inspector must record actual values.

## 1.7   SAFETY PROVISIONS

### 1.7.1   Fire Prevention

Provide a written fire prevention plan for the SPF application.  Address specific fire hazards such as spontaneous combustion from exothermic heat build-up of SPF components during curing.  Provide a continuous fire watch during mixing and spraying of SPF and for a minimum of two hours after completion of work at the end of each day.  Maintain fire watch for additional time as required to ensure no potential ignition conditions exist.

#### 1.7.1.1   Fire Extinguishers

Furnish two fire extinguishers of minimum 15 pounds capacity each, in accordance with NFPA 10, in the immediate vicinity of the work.  CAUTION:  Do not discharge high pressure carbon dioxide extinguishers where explosive vapors exist since the discharge can cause a spark which will ignite the vapors.

### 1.7.2   Respirator Plan

Provide a written respirator plan in accordance with OSHA regulations that protects installers during application and addresses separation of the area to prevent other workers from entering the work area during spraying.

### 1.7.3   Isolation

Isolate the work area as recommended by spray foam manufacturer's written requirements.  Prevent workers without respiratory, skin, and eye Personal Protective Equipment (PPE) or training from entering the work area or otherwise being exposed to off-gassing of the insulation in excess of permissible exposure limits.

### 1.7.4   Respirators and Eye Protection

Respiratory protective devices (respirators) must meet the requirements of ASSE/SAFE Z88.2.  Eye and face protective equipment must meet the requirements of ANSI/ISEA Z87.1.  Additionally, sprayers and workers in the immediate vicinity of the spray must wear NIOSH-approved, full-face, supplied air respirators (SAR) operated in positive pressure or continuous flow mode.  Workers not in the immediate vicinity of the sprayer must wear air purifying respirators (APR) with an organic gas / P100 particulate cartridge.  Instruct personnel in the use of devices.  Maintain such equipment and inspect regularly.  All workers are required to have undergone pulmonary function testing and fit testing and must provide certification that they have done so.  Change APR cartridges in accordance with manufacturer's written recommendations.

### 1.7.5   Clothing and Gloves

Sprayers and workers must wear protective clothing and gloves in accordance with OSHA requirements during materials application.  Disposable coveralls must be worn and must cover all exposed skin.  Sprayers and workers must wear fabric gloves coated with nitrile, neoprene, butyl or PVC.

### 1.7.6   Additional Requirements

Require personnel to review the Health, Safety and Environmental Aspects of Spray Polyurethane Foam and Coverings published by the Spray Polyurethane Foam Alliance (SPFA).  Verify compliance prior to allowing personnel on site for installation work.  http://www.sprayfoam.org.

## 1.8   QUALITY ASSURANCE

### 1.8.1   Qualification of Manufacturer

Submit documentation verifying that the manufacturer of the SPF is currently accredited by the Air Barrier Association of America (ABAA Accreditation https://www.airbarrier.org/) and by the Spray Polyurethane Foam Alliance (SPFA).

### 1.8.2   Qualification of Installer

Submit documentation verifying that installers of the spray foam air barrier are currently certified by ABAA/BPQI (Building Performance Quality Institute) or by the Spray Polyurethane Foam Alliance (SPFA) Professional Certification Program (PCP).  Installers must provide photo identification certification cards for inspection upon request.

### 1.8.3   General Quality Requirements

Provide all products and installation in accordance with SPFA TechDocs requirements (http://www.sprayfoam.org/technical/spfa-technical-documents) and documented best practices.

## 1.9   ENVIRONMENTAL CONDITIONS

### 1.9.1   Temperature and Weather

Install SPF within the range of ambient and substrate surface temperatures in accordance with manufacturer's written instructions.  Do not apply SPF to damp or wet substrates.  Do not apply SPF during inclement weather or when ice, frost, surface moisture, or visible dampness is present on surfaces to be covered, or when precipitation is imminent.  Do not apply SPF to exterior building surfaces when wind speeds exceed 25 miles per hour.  Use moisture measuring methods and equipment to verify that the moisture conditions of substrate surfaces are in accordance with SPF manufacturer requirements prior to application.  Substrate temperatures must be within limits recommended by the manufacturer's printed instructions.

### 1.9.2   Conditions for Primers

Follow manufacturer's printed application and curing instructions.  Do not apply primer when ambient temperature is below 40 degrees F or when ambient temperature is expected to fall below 35 degrees F for the duration of the drying or curing period.

### 1.9.3   Conditions for Ignition Barriers

Ensure that sprayed surfaces comply with manufacturer's written requirements for application coverage, thickness, and curing prior to application of ignition barrier coatings.

### 1.9.4   Temporary Ventilation

Provide temporary ventilation for work of this section in accordance with manufacturer's written instructions and with OSHA requirements for this type of application.

## 1.10   FOAM SPRAY EQUIPMENT

### 1.10.1   Applicator

Use an air purge foam spray gun.

### 1.10.2   Equipment Calibration

Fully calibrate the foam metering equipment to monitor each liquid component to within 2 percent of the SPF manufacturer's required metering ratio.  Calibrate spray equipment each day at the start of operations, after each restart if spraying operations have been terminated for more than one hour, whenever there is a change in fan pattern or pressure, whenever slow curing areas are noticed, whenever a change is made in hose length or working height, and after changeover between materials.  Calibration consists of demonstrating that the equipment is adjusted to deliver components in proper mix and proportion.  Conduct calibration tests on cardboard or plywood on a wall adjacent to the area to be sprayed.

### 1.10.3   Metering Equipment Requirements

Use foam metering equipment capable of developing and maintaining the SPF manufacturer's required liquid component pressures and temperatures.  Foam metering equipment must have gages for visual monitoring.  Equipment must provide temperature control of foam components to within the temperature ranges recommended by the foam manufacturer's printed instructions.

### 1.10.4   Moisture Protection

Protect surfaces of supply containers and tanks used to feed foam metering equipment from moisture.

### 1.10.5   Compressed Air

Supply compressed air that is in contact with SPF during mixing or atomization through moisture traps that are continuously bled.

### 1.10.6   Dispense Excess Materials

Do not deposit materials used for cleaning of equipment or materials dispensed for calibration purposes and establishment of spray gun pattern onto the ground.  Dispense such materials into scrap containers or onto plastic film, or cardboard, and dispose of in accordance with safety requirements and jobsite regulations.

# PART 2   PRODUCTS

## 2.1   PRODUCT SUSTAINABILITY

### 2.1.1   Reduced Volatile Organic Compound (VOC) Content

Provide products with reduced VOC content and provide documentation.

## 2.2   SPRAY FOAM AIR BARRIER

### 2.2.1   General

Provide a closed cell, sprayed in place, SPF that forms a continuous air/vapor/thermal barrier at the building enclosure.  Provide in accordance with ASTM C1029, with the requirements of UFC 3-600-01, ICC IBC Chapter 26, ICC-ES AC377, and NFPA 285.  In the event of a conflict, the most stringent requirement applies.  Provide all system components necessary for a complete, code compliant installation, whether indicated or not, including material support components, expansion and contraction joints, ignition barrier coatings and accessories.

### 2.2.2   Physical Properties

Provide a closed cell product with the following characteristics:

a.  Density (ASTM D1622):  2.0 lb per cf, nominal

b.  Thermal Resistance (ASTM C518)

(1) Initial R-value per inch thickness:  7 sf·degrees F h per Btu

(2) Aged R-value per inch thickness (180 days at 76 degrees F):  6.6 sf·degrees F·h per Btu

c.  Air Permeance (ASTM E2178):  Less than 0.004 CFM per sf at 1.57 psf.

d.  Air Leakage (ASTM E2357, ASTM E283):  Less than 0.004 CFM per sf at 1.57 psf at one inch.

e.  Compressive Strength (ASTM D1621):  Minimum 28.3 psi

f.  Tensile Strength (ASTM D1623)

(1) Medium density:  15 psi

(2) Roofing:  40 psi

g.  Water Vapor Permeance (ASTM E96/E96M, water method): less than 1.2 US Perms at one inch thickness

h.  Vapor Retarder (ICC IBC, ICC IECC) Class III

i.  Surface Burning Characteristics (ASTM E84) 3 inch thickness:

(1) Flame Spread (FS) Index Rating less than 75.

(2) Smoke Developed (SD) Index Rating less than 150.  SPF with an SD rating greater than 150 but less than 450 may be used when fully encapsulated.  Approval of SPF product is contingent upon approval of encapsulation products and assemblies.

j.  Closed Cell Content (ASTM D6226):  90 percent

k.  Dimensional Stability (Humid Aging) (ASTM D2126):  15 percent at 28 days at 158 degrees F with 97 percent relative humidity.

l.  Water Absorption (ASTM D2842):  Maximum 1.0 per volume

m.  Fungi Resistance (ASTM C1338):  Pass, with no growth

n.  Recycled Content:  Minimum 9 percent (pre- and post-consumer)

### 2.2.3   Expansion and Contraction

Provide an assembly that allows for relative movement due to temperature, moisture, and air pressure changes.  Provide expansion and contraction measures as required by the manufacturer's written recommendations.

### 2.2.4   Fire-ratings, Flame Spread and Smoke Developed Index Ratings

Where fire-rated materials are indicated, provide products with the appropriate markings of a qualified testing agency.  Submit fire-rating test reports.  Submit flame spread (FS) and smoke developed (SD) index data.  Where FS and SD values of foam products do not meet requirements, provide corresponding ignition barrier products or assemblies and verify complete encapsulation of the spray foam air barrier through product data or on shop drawings.  Submit for approval in accordance with Section 01 33 00 SUBMITTAL PROCEDURES.

### 2.2.5   Prohibited Materials

Products that contain hexabromocyclododecane (HBCD) flame retardants are prohibited.  Products that contain hydrochlorofluorocarbons (HCFCs), chlorofluorocarbons (CFCs), or other high ozone depleting blowing agents, are prohibited.  For a list of acceptable substitute foam blowing agents see https://www.epa.gov/snap/foam-blowing-agents.

### 2.2.6   Ignition Barrier

Provide a ignition barrier in locations where SPF is exposed to the interior of the building, including occupied attics and plenum spaces.  Provide ignition barriers in accordance with ICC IBC Chapter 26 "Plastics," with ICC-ES AC377, ASTM E736, and NFPA 275.  Choose one or more of the following methods of separation:

Provide a liquid applied, water based polymer intumescent coating in accordance with IBC Section 2603.4.1.6.  The ignition barrier must be consistent with the requirements for the type of construction required by the applicable code and must be installed in a manner so the foam plastic insulation is not exposed.

## 2.3   PRIMERS, ADHESIVES, AND MASTICS

Provide primers, adhesives, mastics and other accessory materials as recommended by spray foam manufacturer's printed literature.

## 2.4   JOINT SEALANTS

As specified in Section 07 92 00 JOINT SEALANTS.  Verify compatibility with other system products.

# PART 3   EXECUTION

## 3.1   EXAMINATION

Before installing the spray foam air barrier and with the installer present, examine substrates, areas, and conditions under which SPF will be applied, for compliance with requirements.  Ensure that surfaces are sound, dry, even, and free of oil, grease, dirt, excess mortar or other contaminants.  Ensure that concrete surfaces are cured and dry, smooth without large voids, spalled areas or sharp protrusions.  Correct defects that adversely affect the spray foam application or performance.  Verify that work by other trades is in place and complete prior to application of spray foam.

## 3.2   PREPARATION

### 3.2.1   Substrate Preparation

Clean, prepare, and treat substrate according to manufacturer's written instructions.  Provide clean, dust-free, and dry substrate for spray foam application.

a.  Prepare surfaces by brushing, scrubbing, scraping, or grinding to remove loose mortar, dust, oil, grease, oxidation, mill scale and other contaminants which will affect adhesion of the SPF.

b.  Wipe down metal surfaces to remove release agents or other non-compatible coatings, using clean sponges or rags soaked in a solvent compatible with the SPF.

### 3.2.2   Protection

Protect adjacent areas and surfaces from spray applied materials in accordance with the following:

a.  Mask and cover adjacent areas to protect from over spray.

b.  Ensure required foam stops and back up materials are in place to achieve a complete seal.

c.  Seal off ventilation equipment.  Install temporary ducting and fans to provide required exhaust of spray fumes.  Provide make-up air as required.

d.  Erect barriers, isolate area, and post warning signs to notify non-protected personnel of the requirement to avoid the spray area.

### 3.2.3   Blocking Around Heat Producing Devices

Install non-combustible blocking around heat producing devices as required by spray foam manufacturer.

### 3.2.4   Fire and Explosion Hazards

Prohibit open flames, sparks, welding, and smoking in the application area. Provide and maintain fire extinguishers of appropriate type, size and distance, as required by NFPA, in the application area.  Mix batches in small enough quantities to avoid spontaneous combustion from exothermic heat build-up of SPF components during curing.

### 3.2.5   Warning Signs

Post warning signs adjacent to the work area stating the area is off limits to unauthorized persons and warning of potential hazards.

### 3.2.6   Prime Substrate

Provide as recommended by the manufacturer for each substrate to be primed.  Use primers at full strength.  Do not dilute primers unless required and as recommended in writing by the manufacturer.  Do not use cleaning solvents for thinning primers or other materials.  Ensure that diluted primer(s) meet VOC requirements.

## 3.3   INSTALLATION

### 3.3.1   Sequencing and Coordination

Sequence the work so as to prevent access to the work area by other trades during foam application and curing.  Limit access of non-essential workers during application.  Notify the Contracting Officer’s Representative 24 hours in advance of spraying operations. Ensure expansion and control joints are provided as detailed on the manufacturer's shop drawings to accommodate the expansion of each layer of the air/vapor/thermal envelope.  Provide temporary fire protection of uncured foam, and isolate the work area, until foam application is isolated with a permanent thermal or ignition barrier.

### 3.3.2   Installation of Spray Foam Air Barrier

Install materials in accordance with paragraph SAFETY PROVISIONS, in accordance with manufacturer's recommendations and in accordance with the following:

a.  Use spray equipment that complies with foam manufacturer's recommendations for the specific type of application, and as specified herein.  Record equipment settings on the Daily Work Record.  Each proportioned unit can supply only one spray gun.

b.  Apply only when surfaces and environmental conditions are within limits prescribed by the material manufacturer.

c.  Continuously connect the spray foam air barrier to form a continuous integrated air barrier system around the entire building enclosure.  Seal edges of barrier at junctures with rough openings.

d.  Install within manufacturer's tolerances, but not more than minus 1/4 inch or plus 1/2 inch.

e.  Sequence work so as to completely seal all penetrations resulting from pipes, vents, wires, conduit, electrical fixtures, structural members, or other construction.  If penetrations through the spray foam air barrier are made after the initial SPF application, reapply in accordance with manufacturer's written instructions for such remedial work.

f.  Do not install SPF within 3 inches of heat emitting devices such as light fixtures and chimneys.

g.  Finished surface of SPF must be free of voids and embedded foreign objects.

h.  Remove masking materials and over spray from adjacent areas immediately after foam surface has hardened.  Ensure cleaning methods do not damage work performed by other sections.

i.  Trim, as required, any excess thickness that would interfere with the application of cladding and covering system by other trades.

j.  Clean and restore surfaces soiled or damaged by work of other trades.  Before cleaning and restoring damaged work, consult with other trades for appropriate and approved methods for cleaning and restoration to prevent further damage.

k.  Complete connections to other components and repair any gaps, holes or other damage using material approved by the manufacturer.

l.  Provide expansion joints in the SPF application aligned with expansion joints in the building enclosure, where substrate materials change, and in accordance with manufacturer's recommendations.

m.  Provide a continuous fire watch in accordance with paragraph SAFETY PROVISIONS.

## 3.4   FIELD QUALITY CONTROL

### 3.4.1   General Site Inspections and Testing

Provide site inspections and testing in accordance with ABAA protocol to verify conformance with the manufacturer's instructions, the ABAA QAP Quality Assurance Program (https://www.airbarrier.org/qap/).

a.  Conduct inspections and testing at 5, 50, and 95 percent of completion of this scope of work.  Forward written inspection reports to the Contracting Officer within 5 working days of the inspection and test being performed.

b.  If inspections reveal any defects, promptly remove and replace defective work at no additional expense to the Government.

### 3.4.2   Manufacturer Site Inspections

Manufacturer's technical representative must visit the site during the installation process to ensure the SPF and accessories are being applied in compliance with requirements.  At a minimum, manufacturer's technical representative must be present at work startup and perform field inspection of the first day's completed application and at substantial completion, prior to demobilization.  After each inspection, submit an inspection report signed by the manufacturer's technical representative, to the Contracting Officer within five working days.  The inspection report must note overall quality of work, deficiencies, and recommended corrective actions in detail.  Notify the Contracting Officer’s Representative a minimum of two working days prior to site visits by manufacturer's technical representative.

### 3.4.3   Contractor's Site Inspections

Establish and maintain an inspection procedure to ensure compliance of the foam installation with contract requirements.  Conduct inspections and testing at 5, 50, and 95 percent completion of application.  Forward written inspection reports to the Contracting Officer within five working days of the inspection and test being performed.  Work not in compliance must be promptly removed and replaced or corrected, in an approved manner, at no additional cost to the Government.  Quality control must include, but is not limited to, the following:

a.  Observation of environmental conditions; number and skill level of insulation workers.

b.  Verification of certification, listing, or label.

c.  Verification of proper storage and handling of materials before, during, and after installation.

d.  Inspection of SPF, support structure, primer, expansion joints, ignition barrier, and accessories.

### 3.4.4   Field Peel Adhesion Test

Conduct in accordance with test protocol indicated in Part 1 paragraph FIELD PEEL ADHENSION TEST.

## 3.5   CORRECTION OF DEFICIENCIES

Upon completion of inspection, testing, or sample taking, repair damaged construction, restore substrates and finishes, and protect repaired construction.  Deficiencies found during inspection must be corrected within 48 hours following notification.

## 3.6   CLEANUP OF SPILLS

Conduct cleanup of uncured product spillage in accordance with paragraph SAFETY PROVISIONS and the manufacturer's written safe handling instructions.  In the event of a conflict, the most stringent requirement governs.

## 3.7   PROTECTION AND CLEANING

### 3.7.1   Protection of Installed Work

Protect SPF installation from damage during application and remainder of construction period in accordance with manufacturer's written instructions.  Repair damaged areas to new condition.

### 3.7.2   Cleaning of Adjacent Surfaces

Clean overspray from adjacent construction using cleaning agents and procedures as recommended in writing by the manufacturer of each type of affected construction and as acceptable to same.

-- End of Section --

SECTION 07 92 00

JOINT SEALANTS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

ASTM INTERNATIONAL (ASTM)

ASTM C1193	(2013) Standard Guide for Use of Joint Sealants

ASTM C1521	(2013) Standard Practice for Evaluating Adhesion of Installed Weatherproofing Sealant Joints

ASTM C834	(2014) Latex Sealants

ASTM C920	(2014a) Standard Specification for Elastomeric Joint Sealants

ASTM D1056	(2014) Standard Specification for Flexible Cellular Materials - Sponge or Expanded Rubber

CALIFORNIA DEPARTMENT OF PUBLIC HEALTH (CDPH)

CDPH SECTION 01350	(2004; Add 2004-01) Standard Practice for the Testing Of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers

SCIENTIFIC CERTIFICATION SYSTEMS (SCS)

SCS	SCS Global Services (SCS)Indoor Advantage

SOUTH COAST AIR QUALITY MANAGEMENT DISTRICT (SCAQMD)

SCAQMD Rule 1168	(1989; R 2005) Adhesive and Sealant Applications

UNDERWRITERS LABORATORIES (UL)

UL 2818	(2013) GREENGUARD Certification Program For Chemical Emissions For Building Materials, Finishes And Furnishings

## 1.2   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-03 Product Data

Sealants

Primers

Bond Breakers

Backstops

## 1.3   PRODUCT DATA

Include storage requirements, shelf life, curing time, instructions for mixing and application, and accessories.  Provide manufacturer's Material Safety Data Sheet (MSDS) for each solvent, primer and sealant material proposed.

## 1.4   CERTIFICATIONS

### 1.4.1   Indoor Air Quality Certifications

Submit required indoor air quality certifications in one submittal package.

#### 1.4.1.1   Adhesives and Sealants

Provide products certified to meet indoor air quality requirements by UL 2818 (Greenguard) Gold, SCS Global Services Indoor Advantage Gold or provide validation by other third-party program that products meet the requirements of this paragraph.  Sealants and non-aerosol adhesive products used on the interior of the building (defined as inside of the weatherproofing system) must meet either emissions requirements of CDPH SECTION 01350 (limit requirements for either office or classroom spaces regardless of space type) or VOC content requirements of SCAQMD Rule 1168.  Provide current product certification documentation from certification body.

## 1.5   ENVIRONMENTAL CONDITIONS

Apply sealant when the ambient temperature is between 40 and 90 degrees F.

## 1.6   DELIVERY AND STORAGE

Deliver materials to the jobsite in unopened manufacturers' sealed shipping containers, with brand name, date of manufacture, color, and material designation clearly marked thereon.  Label elastomeric sealant containers to identify type, class, grade, and use. Handle and store materials in accordance with manufacturer's printed instructions.  Prevent exposure to foreign materials or subjection to sustained temperatures exceeding 90 degrees F or lower than 0 degrees F.  Keep materials and containers closed and separated from absorptive materials such as wood and insulation.

## 1.7   QUALITY ASSURANCE

### 1.7.1   Compatibility with Substrate

Verify that each sealant is compatible for use with each joint substrate in accordance with sealant manufacturer's printed recommendations for each application.

### 1.7.2   Joint Tolerance

Provide joint tolerances in accordance with manufacturer's printed instructions.

### 1.7.3   Adhesion

Provide in accordance with ASTM C1193 or ASTM C1521.

# PART 2   PRODUCTS

## 2.1   SEALANTS

Provide sealant products that have been tested, found suitable, and documented as such by the manufacturer for the particular substrates to which they will be applied.

### 2.1.1   Interior Sealants

Provide ASTM C834.  Provide certification of indoor air quality for interior sealants.  Location(s) and color(s) of sealant for the following.

| LOCATION | COLOR |
| --- | --- |
| a. All Locations | Gray |

### 2.1.2   Exterior Sealants

For joints in vertical surfaces, provide ASTM C920, Type S or M, Grade NS, Class 25, Use NT.  For joints in horizontal surfaces, provide ASTM C920, Type S or M, Grade P, Class 25, Use T.  Provide location(s) and color(s) of sealant as follows.  Note, color "as selected" refers to manufacturer's full range of color options:

| LOCATION | COLOR |
| --- | --- |
| a. All Locations | Match Adjacent Surface Color |

## 2.2   PRIMERS

Non-staining, quick drying type and consistency as recommended by the sealant manufacturer for the particular application.  Provide primers for interior applications that meet the indoor air quality requirements of the paragraph SEALANTS above.

## 2.3   BOND BREAKERS

Type and consistency as recommended by the sealant manufacturer to prevent adhesion of the sealant to the backing or to the bottom of the joint.  Provide bond breakers for interior applications that meet the indoor air quality requirements of the paragraph SEALANTS above.

## 2.4   BACKSTOPS

Provide glass fiber roving, neoprene, butyl, polyurethane, or polyethylene foams free from oil or other staining elements as recommended by sealant manufacturer.  Provide 25 to 33 percent oversized backing for closed cell and 40 to 50 percent oversized backing for open cell material, unless otherwise indicated.  Provide backstop material that is compatible with sealant.  Do not use oakum or other types of absorptive materials as backstops.

### 2.4.1   Rubber

Provide in accordance with ASTM D1056, Type 2, closed cell, Class A, Grade round cross section for cellular rubber sponge backing.

### 2.4.2   Neoprene

Provide in accordance with ASTM D1056, closed cell expanded neoprene cord Type 2, Class C, Grade 2C2 neoprene backing.

## 2.5   CLEANING SOLVENTS

Provide type(s) recommended by the sealant manufacturer and in accordance with environmental requirements herein.  Protect adjacent aluminum and bronze surfaces from solvents.  Provide solvents for interior applications that meet the indoor air quality requirements of the paragraph SEALANTS above.

# PART 3   EXECUTION

## 3.1   FIELD QUALITY CONTROL

Perform a field adhesion test in accordance with manufacturer's instructions and ASTM C1193, Method A or ASTM C1521, Method A, Tail Procedure.  Remove sealants that fail adhesion testing; clean substrates, reapply sealants, and re-test. Test sealants adjacent to failed sealants.  Submit field adhesion test report indicating tests, locations, dates, results, and remedial actions taken.

## 3.2   SURFACE PREPARATION

Prepare surfaces according to manufacturer's printed installation instructions.  Clean surfaces from dirt, frost, moisture, grease, oil, wax, lacquer, paint, or other foreign matter that would destroy or impair adhesion.  Remove oil and grease with solvent; thoroughly remove solvents prior to sealant installation.  Wipe surfaces dry with clean cloths.  When resealing an existing joint, remove existing caulk or sealant prior to applying new sealant.  For surface types not listed below, provide in accordance with sealant manufacturer's printed instructions for each specific surface.

### 3.2.1   Steel Surfaces

Remove loose mill scale by sandblasting or, if sandblasting is impractical or would damage finished work, scraping and wire brushing.  Remove protective coatings by sandblasting or using a residue free solvent.  Remove resulting debris and solvent residue prior to sealant installation.

### 3.2.2   Aluminum or Bronze Surfaces

Remove temporary protective coatings from surfaces that will be in contact with sealant.  When masking tape is used as a protective coating, remove tape and any residual adhesive prior to sealant application.  For removing protective coatings and final cleaning, use non-staining solvents recommended by the manufacturer of the item(s) containing aluminum or bronze surfaces.

### 3.2.3   Concrete and Masonry Surfaces

Where surfaces have been treated with curing compounds, oil, or other such materials, remove materials by sandblasting or wire brushing.  Remove laitance, efflorescence and loose mortar from the joint cavity.  Remove resulting debris prior to sealant installation.

### 3.2.4   Wood Surfaces

Ensure wood surfaces that will be in contact with sealants are free of splinters, sawdust and other loose particles.

## 3.3   SEALANT PREPARATION

Do not add liquids, solvents, or powders to sealants.  Mix multicomponent elastomeric sealants in accordance with manufacturer's printed instructions.

## 3.4   APPLICATION

### 3.4.1   Joint Width-To-Depth Ratios

Acceptable Ratios:

| JOINT WIDTH | JOINT DEPTH |
| --- | --- |
|  | Minimum | Maximum |
| For metal or other nonporous surfaces: |
| 1/4 inch (minimum) | 1/4 inch | 1/4 inch |
| over 1/4 inch | 1/2 of width | Equal to width |
| For wood, concrete, masonry: |
| 1/4 inch (minimum) | 1/4 inch | 1/4 inch |
| over 1/4 inch to 1/2 inch | 1/4 inch | Equal to width |
| over 1/2 inch to 1 inch | 1/2 inch | 5/8 inch |
| Over 1 inch | prohibited |

Unacceptable Ratios:  Where joints of acceptable width-to-depth ratios have not been provided, clean out joints to acceptable depths and grind or cut to acceptable widths without damage to the adjoining work.  Grinding is prohibited at metal surfaces.

### 3.4.2   Unacceptable Sealant Use

Do not install sealants in lieu of other required building enclosure weatherproofing components such as flashing, drainage components, and joint closure accessories, or to close gaps between walls, floors, roofs, windows, and doors, that exceed acceptable installation tolerances.  Remove sealants that have been used in an unacceptable manner and correct building enclosure deficiencies to comply with contract documents requirements.

### 3.4.3   Masking Tape

Place masking tape on the finished surface on one or both sides of joint cavities to protect adjacent finished surfaces from primer or sealant smears.  Remove masking tape within 10 minutes of joint filling and tooling.

### 3.4.4   Backstops

Provide backstops dry and free of tears or holes.  Tightly pack the back or bottom of joint cavities with backstop material to provide joints in specified depths.  Provide backstops where indicated and where backstops are not indicated but joint cavities exceed the acceptable maximum depths specified in JOINT WIDTH-TO-DEPTH RATIOS Table.

### 3.4.5   Primer

Clean out loose particles from joints immediately prior to application of.  Apply primer to joints in concrete masonry units, wood, and other porous surfaces in accordance with sealant manufacturer's printed instructions.  Do not apply primer to exposed finished surfaces.

### 3.4.6   Bond Breaker

Provide bond breakers to surfaces not intended to bond in accordance with, sealant manufacturer's printed instructions for each type of surface and sealant combination specified.

### 3.4.7   Sealants

Provide sealants compatible with the material(s) to which they are applied. Do not use a sealant that has exceeded its shelf life or has jelled and cannot be discharged in a continuous flow from the sealant gun.  Apply sealants in accordance with the manufacturer's printed instructions with a gun having a nozzle that fits the joint width.  Work sealant into joints so as to fill the joints solidly without air pockets.  Tool sealant after application to ensure adhesion.  Apply sealant uniformly smooth and free of wrinkles.  Upon completion of sealant application, roughen partially filled or unfilled joints, apply additional sealant, and tool smooth as specified.  Apply sealer over sealants in accordance with the sealant manufacturer's printed instructions.

## 3.5   PROTECTION AND CLEANING

### 3.5.1   Protection

Protect areas adjacent to joints from sealant smears.  Masking tape may be used for this purpose if removed 5 to 10 minutes after the joint is filled and no residual tape marks remain.

### 3.5.2   Final Cleaning

Upon completion of sealant application, remove remaining smears and stains and leave the work in a clean and neat condition.

a.  Masonry and Other Porous Surfaces:  Immediately remove fresh sealant that has been smeared on adjacent masonry, rub clean with a solvent, and remove solvent residue, in accordance with sealant manufacturer's printed instructions.  Allow excess sealant to cure for 24 hour then remove by wire brushing or sanding.  Remove resulting debris.

b.  Metal and Other Non-Porous Surfaces:  Remove excess sealant with a solvent moistened cloth.  Remove solvent residue in accordance with solvent manufacturer's printed instructions.

-- End of Section --

SECTION 09 29 00

GYPSUM BOARD

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

ANSI A108.11	(1992; Reaffirmed 2005) Specifications for Interior Installation of Cementitious Backer Units

ASTM INTERNATIONAL (ASTM)

ASTM C1002	(2014) Standard Specification for Steel Self-Piercing Tapping Screws for the Application of Gypsum Panel Products or Metal Plaster Bases to Wood Studs or Steel Studs

ASTM C1047	(2014a) Standard Specification for Accessories for Gypsum Wallboard and Gypsum Veneer Base

ASTM C1396/C1396M	(2014a) Standard Specification for Gypsum Board

ASTM C475/C475M	(2015) Joint Compound and Joint Tape for Finishing Gypsum Board

ASTM C840	(2016) Standard Specification for Application and Finishing of Gypsum Board

ASTM C954	(2015) Steel Drill Screws for the Application of Gypsum Panel Products or Metal Plaster Bases to Steel Studs from 0.033 in. (0.84 mm) to 0.112 in. (2.84 mm) in Thickness

CALIFORNIA DEPARTMENT OF PUBLIC HEALTH (CDPH)

CDPH SECTION 01350	(2004; Add 2004-01) Standard Practice for the Testing Of Volatile Organic Emissions from Various Sources Using Small-Scale Environmental Chambers

GYPSUM ASSOCIATION (GA)

GA 214	(2010) Recommended Levels of Gypsum Board Finish

GA 216	(2010) Application and Finishing of Gypsum Panel Products

SCIENTIFIC CERTIFICATION SYSTEMS (SCS)

SCS	SCS Global Services (SCS) Indoor Advantage

UNDERWRITERS LABORATORIES (UL)

UL 2818	(2013) GREENGUARD Certification Program For Chemical Emissions For Building Materials, Finishes And Furnishings

## 1.2   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-03 Product Data

Accessories

Submit for each type of gypsum board.

Certifications

Gypsum Board

SD-07 Certificates

Asbestos Free Materials

Certify that gypsum board types, gypsum backing board types, cementitious backer units, and joint treating materials do not contain asbestos.

Indoor Air Quality

SD-08 Manufacturer's Instructions

Material Safety Data Sheets

SD-10 Operation and Maintenance Data

Manufacturer Maintenance Instructions

SD-11 Closeout Submittals

Recycled Content for Gypsum Board

Indoor Air Quality for Gypsum Board

VOC Content of Joint Compound

## 1.3   CERTIFICATIONS

### 1.3.1   Indoor Air Quality Certifications

Submit required indoor air quality certifications in one submittal package.

#### 1.3.1.1   Ceiling and Wall Systems

Provide products certified to meet indoor air quality requirements by UL 2818 (Greenguard) Gold, SCS Global Services Indoor Advantage Gold or provide validation by other third-party program that products meet the requirements of this paragraph.  Provide current product certification documentation from certification body.  Gypsum wall board and panels must meet the emissions requirements of CDPH SECTION 01350 (limit requirements for either office or classroom spaces regardless of space type).

## 1.4   DELIVERY, STORAGE, AND HANDLING

### 1.4.1   Delivery

Deliver materials in the original packages, containers, or bundles with each bearing the brand name, applicable standard designation, and name of manufacturer, or supplier.

### 1.4.2   Storage

Keep materials dry by storing inside a sheltered building.  Where necessary to store gypsum board and cementitious backer units outside, store off the ground, properly supported on a level platform, and protected from direct exposure to rain, snow, sunlight, and other extreme weather conditions.  Provide adequate ventilation to prevent condensation.  Store per manufacturer's recommendations for allowable temperature and humidity range.  Do not store gypsum wallboard with materials which have high emissions of volatile organic compounds (VOCs) or other contaminants.  Do not store panels near materials that may offgas or emit harmful fumes, such as kerosene heaters, fresh paint, or adhesives.  Do not use materials that have visible moisture or biological growth.

### 1.4.3   Handling

Neatly stack gypsum board and cementitious backer units flat to prevent sagging or damage to the edges, ends, and surfaces.

## 1.5   QUALIFICATIONS

Furnish type of gypsum board work specialized by the installer with a minimum of 3 years of documented successful experience.

## 1.6   SCHEDULING

The gypsum wallboard must be taped, finished and primed before the installation of the highly-emitting materials.

Commence application only after the area scheduled for gypsum board work is completely weathertight.  The heating, ventilating, and air-conditioning systems must be complete and in operation prior to application of the gypsum board.  If the mechanical system cannot be activated before gypsum board is begun, the gypsum board work may proceed in accordance with an approved plan to maintain the environmental conditions specified below.  Apply gypsum board prior to the installation of finish flooring and acoustic ceiling.

## 1.7   ENVIRONMENTAL REQUIREMENTS

Do not expose the gypsum board to excessive sunlight prior to gypsum board application.  Maintain a continuous uniform temperature of not less than 50 degrees F and not more than 80 degrees F for at least one week prior to the application of gypsum board work, while the gypsum board application is being done, and for at least one week after the gypsum board is set.  Shield air supply and distribution devices to prevent any uneven flow of air across the plastered surfaces.  Provide ventilation to exhaust moist air to the outside during gypsum board application, set, and until gypsum board jointing is dry.  In glazed areas, keep windows open top and bottom or side to side 3 to 4 inches.  Reduce openings in cold weather to prevent freezing of joint compound when applied.  For enclosed areas lacking natural ventilation, provide temporary mechanical means for ventilation.  In unglazed areas subjected to hot, dry winds or temperature differentials from day to night of 20 degrees F or more, screen openings with cheesecloth or similar materials.  Avoid rapid drying.  During periods of low indoor humidity, provide minimum air circulation following gypsum boarding and until gypsum board jointing complete and is dry.

# PART 2   PRODUCTS

## 2.1   PRODUCT SUSTAINABILITY CRITERIA

For products in this section, where applicable and to extent allowed by performance criteria, provide and document the following:

## 2.2   MATERIALS

Conform to specifications, standards and requirements specified.  Provide gypsum board types, gypsum backing board types, cementitious backing units, and joint treating materials manufactured from asbestos free materials only.  Submit Material Safety Data Sheets and manufacturer maintenance instructions for gypsum materials including adhesives.

### 2.2.1   Gypsum Board

ASTM C1396/C1396M.  Gypsum board must contain a minimum of 10 percent post-consumer recycled content, or a minimum of 40 percent post-industrial recycled content.  Provide data identifying percentage of recycled content for gypsum board.  Provide certification of indoor air quality for gypsum board.

### 2.2.2   Regular Water-Resistant Gypsum Backing Board

ASTM C1396/C1396M

#### 2.2.2.1   Regular

48 inch wide, 1/2 inch thick, tapered edges.

### 2.2.3   Joint Treatment Materials

ASTM C475/C475M.  Product must be low emitting VOC types with VOC limits not exceeding 50 g/L.  Provide data identifying VOC content of joint compound.

#### 2.2.3.1   Embedding Compound

Specifically formulated and manufactured for use in embedding tape at gypsum board joints and compatible with tape, substrate and fasteners.

#### 2.2.3.2   Finishing or Topping Compound

Specifically formulated and manufactured for use as a finishing compound.

#### 2.2.3.3   All-Purpose Compound

Specifically formulated and manufactured to serve as both a taping and a finishing compound and compatible with tape, substrate and fasteners.

#### 2.2.3.4   Setting or Hardening Type Compound

Specifically formulated and manufactured for use with fiber glass mesh tape.

#### 2.2.3.5   Joint Tape

Use cross-laminated, tapered edge, reinforced paper, or fiber glass mesh tape recommended by the manufacturer.

### 2.2.4   Fasteners

#### 2.2.4.1   Screws

ASTM C1002, Type "G", Type "S" or Type "W" steel drill screws for fastening gypsum board to gypsum board, wood framing members and steel framing members less than 0.033 inch thick.  ASTM C954 steel drill screws for fastening gypsum board to steel framing members 0.033 to 0.112 inch thick.  Provide cementitious backer unit screws with a polymer coating.

### 2.2.5   Accessories

ASTM C1047.  Fabricate from corrosion protected steel or plastic designed for intended use.  Accessories manufactured with paper flanges are not acceptable.  Flanges must be free of dirt, grease, and other materials that may adversely affect bond of joint treatment.  Provide prefinished or job decorated materials.

### 2.2.6   Water

Provide clean, fresh, and potable water.

# PART 3   EXECUTION

## 3.1   EXAMINATION

### 3.1.1   Framing and Furring

Verify that framing and furring are securely attached and of sizes and spacing to provide a suitable substrate to receive gypsum board and cementitious backer units.  Verify that all blocking, headers and supports are in place to support plumbing fixtures and to receive soap dishes, grab bars, towel racks, and similar items.  Do not proceed with work until framing and furring are acceptable for application of gypsum board and cementitious backer units.

### 3.1.2   Building Construction Materials

Do not install building construction materials that show visual evidence of biological growth.

## 3.2   APPLICATION OF GYPSUM BOARD

Apply gypsum board to framing and furring members in accordance with ASTM C840 or GA 216 and the requirements specified.  Apply gypsum board with separate panels in moderate contact; do not force in place.  Stagger end joints of adjoining panels.  Neatly fit abutting end and edge joints.  Use gypsum board of maximum practical length; select panel sizes to minimize waste.  Cut out gypsum board to make neat, close, and tight joints around openings.  In vertical application of gypsum board, provide panels in lengths required to reach full height of vertical surfaces in one continuous piece.  Lay out panels to minimize waste; reuse cutoffs whenever feasible.  Surfaces of gypsum board and substrate members may not be bonded together with an adhesive.  Treat edges of cutouts for plumbing pipes, screwheads, and joints with water-resistant compound as recommended by the gypsum board manufacturer.  Minimize framing by floating corners with single studs and drywall clips.  Install 5/8 inch gypsum board over framing at 16 inch on center.  Provide type of gypsum board for use in each system specified herein as indicated.

### 3.2.1   Application of Gypsum Board to Wood Framing and Furring

Apply in accordance with ASTM C840, System I or GA 216.

### 3.2.2   Control Joints

Install expansion and contraction joints in ceilings and walls in accordance with ASTM C840, System XIII or GA 216.  Fill control joints between studs in fire-rated construction with firesafing insulation to match the fire-rating of construction.

## 3.3   APPLICATION OF CEMENTITIOUS BACKER UNITS

### 3.3.1   Joint Treatment

ANSI A108.11.

## 3.4   FINISHING OF GYPSUM BOARD

Tape and finish gypsum board in accordance with ASTM C840, GA 214 and GA 216.  Finish plenum areas above ceilings to Level 1 in accordance with GA 214.  Finish water resistant gypsum backing board, ASTM C1396/C1396M, to receive ceramic tile to Level 2 in accordance with GA 214.  Finish walls and ceilings to receive a heavy-grade wall covering or heave textured finish before painting to Level 3 in accordance with GA 214.  Finish walls and ceilings without critical lighting to receive flat paints, light textures, or wall coverings to Level 4 in accordance with GA 214.  Unless otherwise specified, finish all gypsum board walls, partitions and ceilings to Level 5 in accordance with GA 214.  Provide joint, fastener depression, and corner treatment.  Tool joints as smoothly as possible to minimize sanding and dust.  Do not use self-adhering fiber glass mesh tape with conventional drying type joint compounds; use setting or hardening type compounds only.  Provide treatment for water-resistant gypsum board as recommended by the gypsum board manufacturer.  Protect workers, building occupants, and HVAC systems from gypsum dust.

### 3.4.1   Uniform Surface

Wherever gypsum board is to receive eggshell, semigloss or gloss paint finish, or where severe, up or down lighting conditions occur, finish gypsum wall surface in accordance to GA 214 Level 5.  In accordance with GA 214 Level 5, apply a thin skim coat of joint compound to the entire gypsum board surface, after the two-coat joint and fastener treatment is complete and dry.

## 3.5   SEALING

Seal openings around pipes, fixtures, and other items projecting through gypsum board and cementitious backer units as specified in Section 07 92 00 JOINT SEALANTS.  Apply material with exposed surface flush with gypsum board or cementitious backer units.

## 3.6   PATCHING

Patch surface defects in gypsum board to a smooth, uniform appearance, ready to receive finishes.

-- End of Section --

SECTION 09 51 00

ACOUSTICAL CEILINGS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AMERICAN SOCIETY OF CIVIL ENGINEERS (ASCE)

ASCE 7	(2010; Errata 2011; Supp 1 2013) Minimum Design Loads for Buildings and Other Structures

ASTM INTERNATIONAL (ASTM)

ASTM A641/A641M	(2009a; R 2014) Standard Specification for Zinc-Coated (Galvanized) Carbon Steel Wire

ASTM C423	(2009a) Sound Absorption and Sound Absorption Coefficients by the Reverberation Room Method

ASTM C635/C635M	(2013a) Manufacture, Performance, and Testing of Metal Suspension Systems for Acoustical Tile and Lay-In Panel Ceilings

ASTM C636/C636M	(2013) Standard Practice for Installation of Metal Ceiling Suspension Systems for Acoustical Tile and Lay-In Panels

ASTM C834	(2014) Latex Sealants

ASTM E1414/E1414M	(2011a; E 2014) Airborne Sound Attenuation Between Rooms Sharing a Common Ceiling Plenum

ASTM E1477	(1998a; R 2013) Luminous Reflectance Factor of Acoustical Materials by Use of Integrating-Sphere Reflectometers

ASTM E795	(2016) Standard Practices for Mounting Test Specimens During Sound Absorption Tests

UNDERWRITERS LABORATORIES (UL)

UL Fire Resistance	(2014) Fire Resistance Directory

## 1.2   SYSTEM DESCRIPTION

Provide sound controlling units mechanically mounted on a ceiling suspension system for acoustical treatment.  The unit size, texture, finish, and color must be as specified.

### 1.2.1   Ceiling Attenuation Class and Test

Provide a ceiling system with an attenuation class (CAC) of 35 for when determined in accordance with ASTM E1414/E1414M.  Provide fixture attenuators over light fixtures and other ceiling penetrations, and provide acoustical blanket insulation adjacent to partitions, as required to achieve the specified CAC.  Provide test ceiling continuous at the partition and assembled in the suspension system in the same manner that the ceiling will be installed on the project.

### 1.2.2   Ceiling Sound Absorption

Determine the Noise Reduction Coefficient (NRC) in accordance with ASTM C423 Test Method.

### 1.2.3   Light Reflectance

Determine light reflectance factor in accordance with ASTM E1477 Test Method.

### 1.2.4   Other Submittals Requirements

The following shall be submitted:

a. Manufacturer's data indicating percentage of recycle material in acoustic ceiling tiles to verify affirmative procurement compliance.

b.  Total weight and volume quantities of acoustic ceiling tiles with recycle material.

c.  Reports by an independent testing laboratory attesting that acoustical ceiling systems meet specified sound transmission requirements.  Data attesting to conformance of the proposed system to Underwriters Laboratories requirements for the fire endurance rating listed in UL Fire Resistance may be submitted in lieu of test reports.

d.  Certificate attesting that the mineral based acoustical units furnished for the project contain recycled material and showing an estimated percent of such material.

## 1.3   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-03 Product Data

Acoustical Ceiling Systems

Certification

## 1.4   SUSTAINABLE DESIGN CERTIFICATION

Certification shall be performed annually and shall be current.

## 1.5   DELIVERY, STORAGE. AND HANDLING

Deliver materials to the site in the manufacturer's original unopened containers with brand name and type clearly marked.  Carefully handle and store materials in dry, watertight enclosures.  Immediately before installation, store acoustical units for not less than 24 hours at the same temperature and relative humidity as the space where they will be installed in order to assure proper temperature and moisture acclimation.

## 1.6   ENVIRONMENTAL REQUIREMENTS

Maintain a uniform temperature of not less than 60 degrees F nor more than 85 degrees F and a relative humidity of not more than 70 percent for 24 hours before, during, and 24 hours after installation of acoustical units.

## 1.7   SCHEDULING

Complete and dry interior finish work such as plastering, concrete and terrazzo work before ceiling installation.  Complete mechanical, electrical, and other work above the ceiling line; install and start operating heating, ventilating, and air conditioning systems in order to maintain temperature and humidity requirements.

## 1.8   WARRANTY

Provide manufacturer's standard performance guarantees or warranties that extend beyond a one year period.  Include an agreement to repair or replace acoustical panels that fail within the warranty period in the standard performance guarantee or warranty.  Failures include, but are not limited to, sagging and warping of panels; rusting and manufacturers defects of grid system.

## 1.9   EXTRA MATERIALS

Furnish five spare tiles, from the same lot as those installed.

# PART 2   PRODUCTS

## 2.1   ACOUSTICAL UNITS

### 2.1.1   Units for Exposed-Grid System

#### 2.1.1.1   Type

I (cellulose composition)

#### 2.1.1.2   Flame Spread

Class A, 25 or less

#### 2.1.1.3   Pattern

#### 2.1.1.4   Minimum NRC

0.50 when tested on mounting Type E-400 of ASTM E795.

#### 2.1.1.5   Minimum Light Reflectance Coefficient

LR-1, 0.75 or greater

#### 2.1.1.6   Nominal Size

24 by 24 inch

#### 2.1.1.7   Edge Detail

Square

#### 2.1.1.8   Finish

Factory-applied standard finish.

#### 2.1.1.9   Minimum CAC

40

## 2.2   SUSPENSION SYSTEM

Provide suspension system conforming to ASTM C635/C635M for intermediate-duty systems.  Provide surfaces exposed to view of aluminum or steel with a factory-applied white baked-enamel finish.  Provide wall molding having a flange of not less than 15/16 inch.  Provide standard mitered corners.  Suspended ceiling framing system must have the capability to support the finished ceiling, light fixtures, air diffusers, and accessories, as shown.  Provide a suspension system with a maximum deflection of 1/360 of the span length.

## 2.3   HANGERS

Provide hangers and attachment capable of supporting a minimum 300 pound ultimate vertical load without failure of supporting material or attachment in accordance with ASCE 7.

### 2.3.1   Wires

Conform wires to ASTM A641/A641M, Class 1, 0.08 inch (12 gauge)inch in diameter.

## 2.4   FINISHES

Use manufacturer's standard textures, patterns and finishes as specified for acoustical units and suspension system members.  Treat ceiling suspension system components to inhibit corrosion.

## 2.5   COLORS AND PATTERNS

Use colors and patterns for acoustical units and suspension system components as specified herein.

## 2.6   ACOUSTICAL SEALANT

Conform acoustical sealant to ASTM C834, nonstaining.

# PART 3   EXECUTION

## 3.1   INSTALLATION

Complete and dry interior finish work such as plastering, concrete, and terrazzo work before installation.  Complete and approve mechanical, electrical, and other work above the ceiling line prior to the start of acoustical ceiling installation.  Provide acoustical work complete with necessary fastenings, clips, and other accessories required for a complete installation.  Do not expose mechanical fastenings in the finished work.  Lay out hangers for each individual room or space.  Provide hangers to support framing around beams, ducts, columns, grilles, and other penetrations through ceilings.  Keep main runners and carrying channels clear of abutting walls and partitions.  Provide at least two main runners for each ceiling span.  Wherever required to bypass an object with the hanger wires, install a subsuspension system so that all hanger wires will be plumb.

### 3.1.1   Suspension System

Install suspension system in accordance with ASTM C636/C636M and as specified herein.  Do not suspend hanger wires or other loads from underside of steel decking.

#### 3.1.1.1   Plumb Hangers

Install hangers plumb and not pressing against insulation covering ducts and pipes.  Where lighting fixtures are supported from the suspended ceiling system, provide hangers at a minimum of four hangers per fixture and located not more than 6 inch from each corner of each fixture.

#### 3.1.1.2   Splayed Hangers

Where hangers must be splayed (sloped or slanted) around obstructions, offset the resulting horizontal force by bracing, countersplaying, or other acceptable means.

### 3.1.2   Wall Molding

Provide wall molding where ceilings abut vertical surfaces.  Miter corners where wall moldings intersect or install corner caps.  Secure wall molding not more than 3 inch from ends of each length and not more than 16 inch on centers between end fastenings.  Provide wall molding springs at each acoustical unit in semi-exposed or concealed systems.

### 3.1.3   Acoustical Units

Install acoustical units in accordance with the approved installation instructions of the manufacturer.  Ensure that edges of acoustical units are in close contact with metal supports, with each other, and in true alignment.  Arrange acoustical units so that units less than one-half width are minimized.  Hold units in exposed-grid system in place with manufacturer's standard hold-down clips, if units weigh less than 1 psf or if required for fire resistance rating.

## 3.2   CLEANING

Following installation, clean dirty or discolored surfaces of acoustical units and leave them free from defects.  Remove units that are damaged or improperly installed and provide new units as directed.

-- End of Section --

SECTION 09 90 00

PAINTS AND COATINGS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AMERICAN CONFERENCE OF GOVERNMENTAL INDUSTRIAL HYGIENISTS (ACGIH)

ACGIH 0100	(2015; Suppl 2002-2016) Documentation of the Threshold Limit Values and  Biological Exposure Indices

ASTM INTERNATIONAL (ASTM)

ASTM D235	(2002; R 2012) Mineral Spirits (Petroleum Spirits) (Hydrocarbon Dry Cleaning Solvent)

ASTM D4263	(1983; R 2012) Indicating Moisture in Concrete by the Plastic Sheet Method

ASTM D4444	(2013) Use and Calibration of Hand-Held Moisture Meters

ASTM D523	(2014) Standard Test Method for Specular Gloss

ASTM D6386	(2016) Standard Practice for Preparation of Zinc (Hot-Dip Galvanized) Coated Iron and Steel Product and Hardware Surfaces for Painting

ASTM F1869	(2016) Standard Test Method for Measuring Moisture Vapor Emission Rate of Concrete Subfloor Using Anhydrous Calcium Chloride

MASTER PAINTERS INSTITUTE (MPI)

MPI 101	(Oct 2009) Epoxy Anti-Corrosive Metal Primer

MPI 107	(Oct 2009) Rust Inhibitive Primer (Water-Based)

MPI 108	(Oct 2009) High Build Epoxy Coating, Low Gloss

MPI 113	(Oct 2009) Exterior Pigmented Elastomeric Coating (Water Based)

MPI 146	(Oct 2009) Institutional Low Odor/VOC Interior Latex, MPI Gloss Level 4

MPI 161	(Oct 2009) Exterior W.B. Light Industrial Coating, MPI Gloss Level 3

MPI 164	(Oct 2009) Exterior W.B. Light Industrial Coating, Gloss, MPI Gloss Level 6

MPI 23	(Oct 2009) Surface Tolerant Metal Primer

MPI 50	(Oct 2009) Interior Latex Primer Sealer

MPI 57	(Oct 2009) Interior Oil Modified Urethane Clear Satin

MPI 9	(Oct 2009) Exterior Alkyd, Gloss, MPI Gloss Level 6

MPI 90	(Oct 2009) Interior Wood Stain, Semi-Transparent

MPI 94	(Oct 2009) Exterior Alkyd, Semi-Gloss, MPI Gloss Level 5

MPI 95	(Oct 2009) Quick Drying Primer for Aluminum

SCIENTIFIC CERTIFICATION SYSTEMS (SCS)

SCS SP-01	(2000) Environmentally Preferable Product Specification for Architectural and Anti-Corrosive Paints

SOCIETY FOR PROTECTIVE COATINGS (SSPC)

SSPC 7/NACE No.4	(2007; E 2004) Brush-Off Blast Cleaning

SSPC PA 1	(2016) Shop, Field, and Maintenance Coating of Metals

SSPC PA Guide 3	(1982; E 1995) A Guide to Safety in Paint Application

SSPC QP 1	(2012; E 2012) Standard Procedure for Evaluating Painting Contractors (Field Application to Complex Industrial Structures)

SSPC SP 1	(2015) Solvent Cleaning

SSPC SP 10/NACE No. 2	(2007) Near-White Blast Cleaning

SSPC SP 12/NACE No.5	(2002) Surface Preparation and Cleaning of Metals by Waterjetting Prior to Recoating

SSPC SP 2	(1982; E 2000; E 2004) Hand Tool Cleaning

SSPC SP 3	(1982; E 2004) Power Tool Cleaning

SSPC SP 6/NACE No.3	(2007) Commercial Blast Cleaning

SSPC VIS 1	(2002; E 2004) Guide and Reference Photographs for Steel Surfaces Prepared by Dry Abrasive Blast Cleaning

SSPC VIS 3	(2004) Guide and Reference Photographs for Steel Surfaces Prepared by Hand and Power Tool Cleaning

SSPC VIS 4/NACE VIS 7	(1998; E 2000; E 2004) Guide and Reference Photographs for Steel Surfaces Prepared by Waterjetting

U.S. ENVIRONMENTAL PROTECTION AGENCY (EPA)

EPA Method 24	(2000) Determination of Volatile Matter Content, Water Content, Density, Volume Solids, and Weight Solids of Surface Coatings

U.S. GENERAL SERVICES ADMINISTRATION (GSA)

FED-STD-313	(2014; Rev E) Material Safety Data, Transportation Data and Disposal Data for Hazardous Materials Furnished to Government Activities

## 1.2   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

The current MPI, "Approved Product List" which lists paint by brand, label, product name and product code as of the date of contract award, will be used to determine compliance with the submittal requirements of this specification.  The Contractor may choose to use a subsequent MPI "Approved Product List", however, only one list may be used for the entire contract and each coating system is to be from a single manufacturer.  All coats on a particular substrate must be from a single manufacturer.  No variation from the MPI Approved Products List is acceptable.

Samples of specified materials may be taken and tested for compliance with specification requirements.

In keeping with the intent of Executive Order 13101, "Greening the Government through Waste Prevention, Recycling, and Federal Acquisition", products certified by SCS as meeting SCS SP-01 shall be given preferential consideration over registered products.  Products that are registered shall be given preferential consideration over products not carrying any EPP designation.

SD-03 Product Data

Certification

Coating

Manufacturer's Technical Data Sheets

Indicate VOC content.

SD-04 Samples

Color

Submit manufacturer's samples of paint colors.  Cross reference color samples to color scheme as indicated.

SD-07 Certificates

Qualification Testing laboratory for coatings

SD-08 Manufacturer's Instructions

Manufacturer's Material Safety Data Sheets

Submit manufacturer's Material Safety Data Sheets for coatings, solvents, and other potentially hazardous materials, as defined in FED-STD-313.

SD-10 Operation and Maintenance Data

Coatings

Preprinted cleaning and maintenance instructions for all coating systems shall be provided.

## 1.3   APPLICATOR'S QUALIFICATIONS

### 1.3.1   SSPC QP 1 Certification

All contractors and subcontractors that perform surface preparation or coating application shall be certified by the Society for Protective Coatings (formerly Steel Structures Painting Council) (SSPC) to the requirements of SSPC QP 1 prior to contract award, and shall remain certified while accomplishing any surface preparation or coating application.  The painting contractors and painting subcontractors must remain so certified for the duration of the project.  If a contractor's or subcontractor's certification expires, the firm will not be allowed to perform any work until the certification is reissued.  Requests for extension of time for any delay to the completion of the project due to an inactive certification will not be considered and liquidated damages will apply.  Notify the Contracting Officer of any change in contractor certification status.

## 1.4   REGULATORY REQUIREMENTS

### 1.4.1   Environmental Protection

In addition to requirements specified elsewhere for environmental protection, provide coating materials that conform to the restrictions of the local Air Pollution Control District and regional jurisdiction.  Notify Contracting Officer of any paint specified herein which fails to conform.

### 1.4.2   Lead Content

Do not use coatings having a lead content over 0.06 percent by weight of nonvolatile content.

### 1.4.3   Chromate Content

Do not use coatings containing zinc-chromate or strontium-chromate.

### 1.4.4   Asbestos Content

Materials shall not contain asbestos.

### 1.4.5   Mercury Content

Materials shall not contain mercury or mercury compounds.

### 1.4.6   Silica

Abrasive blast media shall not contain free crystalline silica.

### 1.4.7   Human Carcinogens

Materials shall not contain ACGIH 0100 confirmed human carcinogens (A1) or suspected human carcinogens (A2).

## 1.5   PACKAGING, LABELING, AND STORAGE

Paints shall be in sealed containers that legibly show the contract specification number, designation name, formula or specification number, batch number, color, quantity, date of manufacture, manufacturer's formulation number, manufacturer's directions including any warnings and special precautions, and name and address of manufacturer.  Pigmented paints shall be furnished in containers not larger than 5 gallons.  Paints and thinners shall be stored in accordance with the manufacturer's written directions, and as a minimum, stored off the ground, under cover, with sufficient ventilation to prevent the buildup of flammable vapors, and at temperatures between 40 to 95 degrees F.  Do not store paint, polyurethane, varnish, or wood stain products with materials that have a high capacity to adsorb VOC emissions.  Do not store paint, polyurethane, varnish, or wood stain products in occupied spaces.

## 1.6   SAFETY AND HEALTH

Apply coating materials using safety methods and equipment in accordance with the following:

Work shall comply with applicable Federal, State, and local laws and regulations, including the Activity The Activity Hazard Analysis shall include analyses of the potential impact of painting operations on painting personnel and on others involved in and adjacent to the work zone.

### 1.6.1   Safety Methods Used During Coating Application

Comply with the requirements of SSPC PA Guide 3.

## 1.7   ENVIRONMENTAL CONDITIONS

Comply, at minimum, with manufacturer recommendations for space ventilation during and after installation.

### 1.7.1   Coatings

Do not apply coating when air or substrate conditions are:

a.  Less than 5 degrees F above dew point;

b.  Below 50 degrees F  or over 95 degrees F, unless specifically pre-approved by the Contracting Officer and the product manufacturer.  Under no circumstances shall application conditions exceed manufacturer recommendations.

### 1.7.2   Post-Application

Vacate space for as long as possible after application.  Wait a minimum of 48 hours before occupying freshly painted rooms.  Maintain one of the following ventilation conditions during the curing period, or for 72 hours after application:

a.  Supply airflow at a rate of 6 air changes per hour, when outside temperatures are between 55 degrees F and 85 degrees F and humidity is between 30 percent and 60 percent.

b.  Supply airflow at a rate of 1.5 air changes per hour, when outside air conditions are not within the range stipulated above.

## 1.8   SCHEDULING

Allow paint to cure prior to the installation of materials that adsorb VOCs.

## 1.9   COLOR SELECTION

Colors of finish coats shall be as indicated or specified.  Where not indicated or specified, colors shall be selected by the Contracting Officer’s Representative.  Manufacturers' names and color identification are used for the purpose of color identification only.  Named products are acceptable for use only if they conform to specified requirements.  Products of other manufacturers are acceptable if the colors approximate colors indicated and the product conforms to specified requirements.

Tint each coat progressively darker to enable confirmation of the number of coats.

Color, texture, and pattern of wall coating systems shall match existing.

## 1.10   LOCATION AND SURFACE TYPE TO BE PAINTED

### 1.10.1   Painting Included

Where a space or surface is indicated to be painted, include the following unless indicated otherwise.

a.  Existing coated surfaces that are damaged during performance of the work.

#### 1.10.1.1   Interior Painting

Includes new surfaces existing coated surfaces of the building and appurtenances as indicated and existing coated surfaces made bare by cleaning operations.

### 1.10.2   Painting Excluded

Do not paint the following unless indicated otherwise.

a.  Surfaces concealed and made inaccessible by panelboards, fixed ductwork, machinery, and equipment fixed in place.

b.  Surfaces in concealed spaces.  Concealed spaces are defined as enclosed spaces above suspended ceilings, furred spaces, attic spaces, crawl spaces, elevator shafts and chases.

c.  Steel to be embedded in concrete.

d.  Copper, stainless steel, aluminum, brass, and lead except existing coated surfaces.

e.  Hardware, fittings, and other factory finished items.

### 1.10.3   Definitions and Abbreviations

#### 1.10.3.1   Qualification Testing

Qualification testing is the performance of all test requirements listed in the product specification.  This testing is accomplished by MPI to qualify each product for the MPI Approved Product List, and may also be accomplished by Contractor's third party testing lab if an alternative to Batch Quality Conformance Testing by MPI is desired.

#### 1.10.3.2   Batch Quality Conformance Testing

Batch quality conformance testing determines that the product provided is the same as the product qualified to the appropriate product specification.  This testing shall only be accomplished by MPI testing lab.

#### 1.10.3.3   Coating

A film or thin layer applied to a base material called a substrate.  A coating may be a metal, alloy, paint, or solid/liquid suspensions on various substrates (metals, plastics, wood, paper, leather, cloth, etc.).  They may be applied by electrolysis, vapor deposition, vacuum, or mechanical means such as brushing, spraying, calendaring, and roller coating.  A coating may be applied for aesthetic or protective purposes or both.  The term "coating" as used herein includes emulsions, enamels, stains, varnishes, sealers, epoxies, and other coatings, whether used as primer, intermediate, or finish coat.  The terms paint and coating are used interchangeably.

#### 1.10.3.4   DFT or dft

Dry film thickness, the film thickness of the fully cured, dry paint or coating.

#### 1.10.3.5   DSD

Degree of Surface Degradation, the MPI system of defining degree of surface degradation.  Five (5) levels are generically defined under the Assessment sections in the MPI Maintenance Repainting Manual.

#### 1.10.3.6   EPP

Environmentally Preferred Products, a standard for determining environmental preferability in support of Executive Order 13101.

#### 1.10.3.7   EXT

MPI short term designation for an exterior coating system.

#### 1.10.3.8   INT

MPI short term designation for an interior coating system.

#### 1.10.3.9   micron / microns

The metric measurement for 0.001 mm or one/one-thousandth of a millimeter.

#### 1.10.3.10   mil / mils

The English measurement for 0.001 in or one/one-thousandth of an inch, equal to 25.4 microns or 0.0254 mm.

#### 1.10.3.11   mm

The metric measurement for millimeter, 0.001 meter or one/one-thousandth of a meter.

#### 1.10.3.12   MPI Gloss Levels

MPI system of defining gloss.  Seven (7) gloss levels (G1 to G7) are generically defined under the Evaluation sections of the MPI Manuals.  Traditionally, Flat refers to G1/G2, Eggshell refers to G3, Semigloss refers to G5, and Gloss refers to G6.

Gloss levels are defined by MPI as follows:

Gloss	Description		Units		Units

Level		at 60 degrees	at 85 degrees

G1	Matte or Flat		0 to 5		10 max

G2	Velvet		0 to 10		10 to 35

G3	Eggshell		10 to 25		10 to 35

G4	Satin		20 to 35		35 min

G5	Semi-Gloss		35 to 70

G6	Gloss		70 to 85

G7	High Gloss

Gloss is tested in accordance with ASTM D523.  Historically, the Government has used Flat (G1 / G2), Eggshell (G3), Semi-Gloss (G5), and Gloss (G6).

#### 1.10.3.13   MPI System Number

The MPI coating system number in each Division found in either the MPI Architectural Painting Specification Manual or the Maintenance Repainting Manual and defined as an exterior (EXT/REX) or interior system (INT/RIN).  The Division number follows the CSI Master Format.

#### 1.10.3.14   Paint

See Coating definition.

#### 1.10.3.15   REX

MPI short term designation for an exterior coating system used in repainting projects or over existing coating systems.

#### 1.10.3.16   RIN

MPI short term designation for an interior coating system used in repainting projects or over existing coating systems.

# PART 2   PRODUCTS

## 2.1   MATERIALS

Conform to the coating specifications and standards referenced in PART 3.  Submit manufacturer's technical data sheets for specified coatings and solvents.  Minimum 20 percent post-consumer recycled content for the following light-colored paints and primers.  Minimum 50 percent post-consumer recycled content for the following dark-colored paints and primers.  All consolidated latex paints shall contain a minimum of 100 percent post-consumer recycled content.  Comply with applicable regulations regarding toxic and hazardous materials.

# PART 3   EXECUTION

## 3.1   PROTECTION OF AREAS AND SPACES NOT TO BE PAINTED

Prior to surface preparation and coating applications, remove, mask, or otherwise protect, hardware, hardware accessories, machined surfaces, radiator covers, plates, lighting fixtures, public and private property, and other such items not to be coated that are in contact with surfaces to be coated.  Following completion of painting, workmen skilled in the trades involved shall reinstall removed items.  Restore surfaces contaminated by coating materials, to original condition and repair damaged items.

## 3.2   SURFACE PREPARATION

Remove dirt, splinters, loose particles, grease, oil, disintegrated coatings, and other foreign matter and substances deleterious to coating performance as specified for each substrate before application of paint or surface treatments.  Oil and grease shall be removed prior to mechanical cleaning.  Cleaning shall be programmed so that dust and other contaminants will not fall on wet, newly painted surfaces.  Exposed ferrous metals such as nail heads on or in contact with surfaces to be painted with water-thinned paints, shall be spot-primed with a suitable corrosion-inhibitive primer capable of preventing flash rusting and compatible with the coating specified for the adjacent areas.

### 3.2.1   Existing Coated Surfaces with Minor Defects

Sand, spackle, and treat minor defects to render them smooth.  Minor defects are defined as scratches, nicks, cracks, gouges, spalls, alligatoring, chalking, and irregularities due to partial peeling of previous coatings.

### 3.2.2   Substrate Repair

a.  Repair substrate surface damaged during coating removal;

b.  Sand edges of adjacent soundly-adhered existing coatings so they are tapered as smooth as practical to areas involved with coating removal; and

c.  Clean and prime the substrate as specified.

## 3.3   PREPARATION OF CONCRETE AND CEMENTITIOUS SURFACE

### 3.3.2   Gypsum Board

a.  Surface Cleaning:  Gypsum board shall be clean and free from loose matter; gypsum board shall be dry.  Remove loose dirt and dust by brushing with a soft brush, rubbing with a dry cloth, or vacuum-cleaning prior to application of the first coat material.  A damp cloth or sponge may be used if paint will be water-based.

b.  Repair of Minor Defects:  Prior to painting, repair joints, cracks, holes, surface irregularities, and other minor defects with patching plaster or spackling compound and sand smooth.

c.  Allowable Moisture Content:  Latex coatings may be applied to damp surfaces, but not surfaces with droplets of water.  Do not apply epoxies to damp surfaces as determined by ASTM D4263.  New plaster to be coated shall have a maximum moisture content of 8 percent, when measured in accordance with ASTM D4444, Method A, unless otherwise authorized. In addition to moisture content requirements, allow new plaster to age a minimum of 30 days before preparation for painting.

## 3.4   APPLICATION

### 3.4.1   Coating Application

Painting practices shall comply with applicable federal, state and local laws enacted to insure compliance with Federal Clean Air Standards.  Apply coating materials in accordance with SSPC PA 1.  SSPC PA 1 methods are applicable to all substrates, except as modified herein.

At the time of application, paint shall show no signs of deterioration.  Uniform suspension of pigments shall be maintained during application.

Unless otherwise specified or recommended by the paint manufacturer, paint may be applied by brush, roller, or spray.  Use trigger operated spray nozzles for water hoses.  Rollers for applying paints and enamels shall be of a type designed for the coating to be applied and the surface to be coated.  Wear protective clothing and respirators when applying oil-based paints or using spray equipment with any paints.

Paints, except water-thinned types, shall be applied only to surfaces that are completely free of moisture as determined by sight or touch.

Thoroughly work coating materials into joints, crevices, and open spaces.  Special attention shall be given to insure that all edges, corners, crevices, welds, and rivets receive a film thickness equal to that of adjacent painted surfaces.

Each coat of paint shall be applied so dry film shall be of uniform thickness and free from runs, drops, ridges, waves, pinholes or other voids, laps, brush marks, and variations in color, texture, and finish.  Hiding shall be complete.

Touch up damaged coatings before applying subsequent coats. Interior areas shall be broom clean and dust free before and during the application of coating material.

a.  Drying Time:  Allow time between coats, as recommended by the coating manufacturer, to permit thorough drying, but not to present topcoat adhesion problems.  Provide each coat in specified condition to receive next coat.

b.  Primers, and Intermediate Coats:  Do not allow primers or intermediate coats to dry more than 30 days, or longer than recommended by manufacturer, before applying subsequent coats. Follow manufacturer's recommendations for surface preparation if primers or intermediate coats are allowed to dry longer than recommended by manufacturers of subsequent coatings.  Each coat shall cover surface of preceding coat or surface completely and there shall be a visually perceptible difference in shades of successive coats.

c.  Finished Surfaces:  Provide finished surfaces free from runs, drops, ridges, waves, laps, brush marks, and variations in colors.

### 3.4.2   Mixing and Thinning of Paints

Reduce paints to proper consistency by adding fresh paint, except when thinning is mandatory to suit surface, temperature, weather conditions, application methods, or for the type of paint being used.  Obtain written permission from the Contracting Officer to use thinners.  The written permission shall include quantities and types of thinners to use.

When thinning is allowed, paints shall be thinned immediately prior to application with not more than 1 pint of suitable thinner per gallon.  The use of thinner shall not relieve the Contractor from obtaining complete hiding, full film thickness, or required gloss.  Thinning shall not cause the paint to exceed limits on volatile organic compounds.  Paints of different manufacturers shall not be mixed.

### 3.4.3   Two-Component Systems

Two-component systems shall be mixed in accordance with manufacturer's instructions.  Any thinning of the first coat to ensure proper penetration and sealing shall be as recommended by the manufacturer for each type of substrate.

### 3.4.4   Coating Systems

a.  Systems by Substrates:  Apply coatings that conform to the respective specifications listed in the following Tables:

Table

Division 9:  Interior, Gypsum Board, Paint Table

b.  Minimum Dry Film Thickness (DFT):  Apply paints, primers, varnishes, enamels, undercoats, and other coatings to a minimum dry film thickness of 1.5 mil each coat unless specified otherwise in the Tables.  Coating thickness where specified, refers to the minimum dry film thickness.

c.  Coatings for Surfaces Not Specified Otherwise:  Coat surfaces which have not been specified, the same as surfaces having similar conditions of exposure.

d.  Existing Surfaces Damaged During Performance of the Work, Including New Patches In Existing Surfaces:  Coat surfaces with the following:

(1)  One coat of primer.

(2)  One coat of undercoat or intermediate coat.

(3)  One topcoat to match adjacent surfaces.

e.  Existing Coated Surfaces To Be Painted:  Apply coatings conforming to the respective specifications listed in the Tables herein, except that pretreatments, sealers and fillers need not be provided on surfaces where existing coatings are soundly adhered and in good condition.  Do not omit undercoats or primers.

## 3.5   COATING SYSTEMS FOR CONCRETE AND CEMENTITIOUS SUBSTRATES

Apply coatings of Tables in Division 3, 4 and 9 for Exterior and Interior.

## 3.6   COATING SYSTEMS FOR WOOD AND PLYWOOD

a.  Apply coatings of Tables in Division 6 for Exterior and Interior.

b.  Apply stains in accordance with manufacturer's printed instructions.

## 3.7   INSPECTION AND ACCEPTANCE

In addition to meeting previously specified requirements, demonstrate mobility of moving components, including swinging and sliding doors, cabinets, and windows with operable sash, for inspection by the Contracting Officer’s Representative.  Perform this demonstration after appropriate curing and drying times of coatings have elapsed and prior to invoicing for final payment.

## 3.8   WASTE MANAGEMENT

As specified in Section “Hazardous Waste” and as follows.  Do not use kerosene or any such organic solvents to clean up water based paints.  Properly dispose of paints or solvents in designated containers. Close and seal partially used containers of paint to maintain quality as necessary for reuse.  Store in protected, well-ventilated, fire-safe area at moderate temperature.  Place materials defined as hazardous or toxic waste in designated containers.  Coordinate with manufacturer for take-back program.  Set aside scrap to be returned to manufacturer for recycling into new product.  When such a service is not available, local recyclers shall be sought after to reclaim the materials.  Where local options exist for leftover paint recycling, collect all waste paint by type and provide for delivery to recycling or collection facility for reuse by local organizations.

## 3.9   PAINT TABLES

All DFT's are minimum values.  Use only materials with a GPS green check mark having a minimum MPI "Environmentally Friendly" rating based on VOC (EPA Method 24) content levels.  Acceptable products are listed in the MPI Green Approved Products List, available at http://www.specifygreen.com/APL/ProductIdxByMPInum.asp.

### 3.9.2   INTERIOR PAINT TABLES

DIVISION 9:  INTERIOR GYPSUM BOARD PAINT TABLE

A.  New and Existing, previously painted Wallboard not otherwise specified:

1. Institutional Low Odor / Low VOC Latex

New; MPI INT 9.2M-G4 (Satin) / Existing; MPI RIN 9.2M-G4 (Satin)

Primer:             Intermediate:       Topcoat:

MPI 50              MPI 146             MPI 146

System DFT:   4 mils

-- End of Section --

SECTION 22 00 00

PLUMBING, GENERAL PURPOSE

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AMERICAN NATIONAL STANDARDS INSTITUTE (ANSI)

ANSI Z21.10.3/CSA 4.3	(2015) Gas Water Heaters Vol. III, Storage Water Heaters With Input Ratings Above 75,000 Btu Per Hour, Circulating and Instantaneous

ANSI Z21.22/CSA 4.4	(2015) Relief Valves for Hot Water Supply Systems

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING ENGINEERS (ASHRAE)

ASHRAE 90.1 - IP	(2013) Energy Standard for Buildings Except Low-Rise Residential Buildings

AMERICAN SOCIETY OF SANITARY ENGINEERING (ASSE)

ASSE 1010	(2004) Performance Requirements for Water Hammer Arresters (ANSI approved 2004)

AMERICAN WATER WORKS ASSOCIATION (AWWA)

AWWA C651	(2014) Standard for Disinfecting Water Mains

AWWA C652	(2011) Disinfection of Water-Storage Facilities

AMERICAN WELDING SOCIETY (AWS)

AWS A5.8/A5.8M	(2011; Amendment 2012) Specification for Filler Metals for Brazing and Braze Welding

AWS B2.2/B2.2M	(2016) Specification for Brazing Procedure and Performance Qualification

ASME INTERNATIONAL (ASME)

ASME A112.6.1M	(1997; R 2017) Floor Affixed Supports for Off-the-Floor Plumbing Fixtures for Public Use

ASME B1.20.1	(2013) Pipe Threads, General Purpose (Inch)

ASME B16.15	(2013) Cast Copper Alloy Threaded Fittings Classes 125 and 250

ASME B16.18	(2012) Cast Copper Alloy Solder Joint Pressure Fittings

ASME B16.22	(2013) Standard for Wrought Copper and Copper Alloy Solder Joint Pressure Fittings

ASME B16.50	(2013) Wrought Copper and Copper Alloy Braze-Joint Pressure Fittings

ASME B31.5	(2016) Refrigeration Piping and Heat Transfer Components

ASME B40.100	(2013) Pressure Gauges and Gauge Attachments

ASME BPVC SEC IV	(2010) BPVC Section IV-Rules for Construction of Heating Boilers

ASME CSD-1	(2016) Control and Safety Devices for Automatically Fired Boilers

ASTM INTERNATIONAL (ASTM)

ASTM B117	(2016) Standard Practice for Operating Salt Spray (Fog) Apparatus

ASTM B306	(2013) Standard Specification for Copper Drainage Tube (DWV)

ASTM B32	(2008; R 2014) Standard Specification for Solder Metal

ASTM B370	(2012) Standard Specification for Copper Sheet and Strip for Building Construction

ASTM B42	(2015a) Standard Specification for Seamless Copper Pipe, Standard Sizes

ASTM B813	(2016) Standard Specification for Liquid and Paste Fluxes for Soldering of Copper and Copper Alloy Tube

ASTM B828	(2016) Standard Practice for Making Capillary Joints by Soldering of Copper and Copper Alloy Tube and Fittings

ASTM B88	(2016) Standard Specification for Seamless Copper Water Tube

ASTM C920	(2014a) Standard Specification for Elastomeric Joint Sealants

ASTM D2564	(2012) Standard Specification for Solvent Cements for Poly(Vinyl Chloride) (PVC) Plastic Piping Systems

ASTM D2665	(2014) Standard Specification for Poly(Vinyl Chloride) (PVC) Plastic Drain, Waste, and Vent Pipe and Fittings

ASTM D2855	(2015) Standard Practice for Making Solvent-Cemented Joints with Poly(Vinyl Chloride) (PVC) Pipe and Fittings

ASTM D3139	(1998; R 2011) Joints for Plastic Pressure Pipes Using Flexible Elastomeric Seals

ASTM D3212	(2007; R 2013) Standard Specification for Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals

ASTM D3311	(2017) Standard Specification for Drain, Waste, and Vent (DWV) Plastic Fittings Patterns

ASTM E1	(2014) Standard Specification for ASTM Liquid-in-Glass Thermometers

ASTM F1760	(2016) Standard Specification for Coextruded Poly(Vinyl Chloride) (PVC) Non-Pressure Plastic Pipe Having Reprocessed-Recycled Content

ASTM F477	(2014) Standard Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe

ASTM F891	(2016) Standard Specification for Coextruded Poly (Vinyl Chloride) (PVC) Plastic Pipe with a Cellular Core

COPPER DEVELOPMENT ASSOCIATION (CDA)

CDA A4015	(2010) Copper Tube Handbook

INTERNATIONAL ASSOCIATION OF PLUMBING AND MECHANICAL OFFICIALS (IAPMO)

IAPMO PS 117	(2005b) Press Type Or Plain End Rub Gasketed W/ Nail CU & CU Alloy Fittings 4 Install On CU Tubing

INTERNATIONAL CODE COUNCIL (ICC)

ICC IPC	(2015) International Plumbing Code

MANUFACTURERS STANDARDIZATION SOCIETY OF THE VALVE AND FITTINGS INDUSTRY (MSS)

MSS SP-110	(2010) Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends

MSS SP-58	(1993; Reaffirmed 2010) Pipe Hangers and Supports - Materials, Design and Manufacture, Selection, Application, and Installation

MSS SP-67	(2017) Butterfly Valves

MSS SP-70	(2011) Gray Iron Gate Valves, Flanged and Threaded Ends

MSS SP-72	(2010a) Ball Valves with Flanged or Butt-Welding Ends for General Service

MSS SP-80	(2013) Bronze Gate, Globe, Angle and Check Valves

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

NEMA 250	(2014) Enclosures for Electrical Equipment (1000 Volts Maximum)

NEMA MG 1	(2016; SUPP 2016) Motors and Generators

NEMA MG 11	(1977; R 2012) Energy Management Guide for Selection and Use of Single Phase Motors

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 90A	(2018) Standard for the Installation of Air Conditioning and Ventilating Systems

NSF INTERNATIONAL (NSF)

NSF/ANSI 14	(2017b) Plastics Piping System Components and Related Materials

NSF/ANSI 61	(2016) Drinking Water System Components - Health Effects

PLASTIC PIPE AND FITTINGS ASSOCIATION (PPFA)

PPFA Fire Man	(2010) Firestopping: Plastic Pipe in Fire Resistive Construction

PLUMBING AND DRAINAGE INSTITUTE (PDI)

PDI WH 201	(2010) Water Hammer Arresters Standard

SOCIETY OF AUTOMOTIVE ENGINEERS INTERNATIONAL (SAE)

SAE J1508	(2009) Hose Clamp Specifications

U.S. DEPARTMENT OF ENERGY (DOE)

Energy Star	(1992; R 2006) Energy Star Energy Efficiency Labeling System (FEMP)

U.S. ENVIRONMENTAL PROTECTION AGENCY (EPA)

EPA SM 9223	(2004) Enzyme Substrate Coliform Test

PL 93-523	(1974; A 1999) Safe Drinking Water Act

U.S. NATIONAL ARCHIVES AND RECORDS ADMINISTRATION (NARA)

10 CFR 430	Energy Conservation Program for Consumer Products

40 CFR 141.80	National Primary Drinking Water Regulations; Control of Lead and Copper; General Requirements

PL 109-58	Energy Policy Act of 2005 (EPAct05)

UNDERWRITERS LABORATORIES (UL)

UL 174	(2004; Reprint Apr 2015) Household Electric Storage Tank Water Heaters

## 1.2   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-03 Product Data

Water Heaters

SD-06 Test Reports

Tests, Flushing and Disinfection

Test reports in booklet form showing all field tests performed to adjust each component and all field tests performed to prove compliance with the specified performance criteria, completion and testing of the installed system.  Each test report shall indicate the final position of controls.

SD-07 Certificates

Materials and Equipment

Where equipment is specified to conform to requirements of the ASME Boiler and Pressure Vessel Code, the design, fabrication, and installation shall conform to the code.

SD-10 Operation and Maintenance Data

Plumbing System

Submit in accordance with Section 01 78 23 OPERATING INSTRUCTIONS AND TRAINING.

## 1.3   STANDARD PRODUCTS

Specified materials and equipment shall be standard products of a manufacturer regularly engaged in the manufacture of such products.  Specified equipment shall essentially duplicate equipment that has performed satisfactorily at least two years prior to bid opening.  Standard products shall have been in satisfactory commercial or industrial use for 2 years prior to bid opening.  The 2-year use shall include applications of equipment and materials under similar circumstances and of similar size.  The product shall have been for sale on the commercial market through advertisements, manufacturers' catalogs, or brochures during the 2 year period.

### 1.3.1   Alternative Qualifications

Products having less than a two-year field service record will be acceptable if a certified record of satisfactory field operation for not less than 6000 hours, exclusive of the manufacturer's factory or laboratory tests, can be shown.

### 1.3.2   Service Support

The equipment items shall be supported by service organizations.  Submit a certified list of qualified permanent service organizations for support of the equipment which includes their addresses and qualifications.  These service organizations shall be reasonably convenient to the equipment installation and able to render satisfactory service to the equipment on a regular and emergency basis during the warranty period of the contract.

### 1.3.3   Manufacturer's Nameplate

Each item of equipment shall have a nameplate bearing the manufacturer's name, address, model number, and serial number securely affixed in a conspicuous place; the nameplate of the distributing agent will not be acceptable.

### 1.3.4   Modification of References

In each of the publications referred to herein, consider the advisory provisions to be mandatory, as though the word, "shall" had been substituted for "should" wherever it appears.  Interpret references in these publications to the "authority having jurisdiction", or words of similar meaning, to mean the Contracting Officer.

#### 1.3.4.1   Definitions

For the International Code Council (ICC) Codes referenced in the contract documents, advisory provisions shall be considered mandatory, the word "should" shall be interpreted as "shall."  Reference to the "code official" shall be interpreted to mean the "Contracting Officer."  For Navy owned property, references to the "owner" shall be interpreted to mean the "Contracting Officer."  For leased facilities, references to the "owner" shall be interpreted to mean the "lessor."  References to the "permit holder" shall be interpreted to mean the "Contractor."

#### 1.3.4.2   Administrative Interpretations

For ICC Codes referenced in the contract documents, the provisions of Chapter 1, "Administrator," do not apply.  These administrative requirements are covered by the applicable Federal Acquisition Regulations (FAR) included in this contract and by the authority granted to the Officer in Charge of Construction to administer the construction of this project.  References in the ICC Codes to sections of Chapter 1, shall be applied appropriately by the Contracting Officer as authorized by his administrative cognizance and the FAR.

## 1.4   DELIVERY, STORAGE, AND HANDLING

Handle, store, and protect equipment and materials to prevent damage before and during installation in accordance with the manufacturer's recommendations, and as approved by the Contracting Officer.  Replace damaged or defective items.

## 1.5   REGULATORY REQUIREMENTS

Unless otherwise required herein, plumbing work shall be in accordance with ICC IPC.  Energy consuming products and systems shall be in accordance with PL 109-58 and ASHRAE 90.1 - IP

## 1.6   PROJECT/SITE CONDITIONS

The Contractor shall become familiar with details of the work, verify dimensions in the field, and advise the Contracting Officer of any discrepancy before performing any work.

## 1.7   INSTRUCTION TO GOVERNMENT PERSONNEL

When specified in other sections, furnish the services of competent instructors to give full instruction to the designated Government personnel in the adjustment, operation, and maintenance, including pertinent safety requirements, of the specified equipment or system.  Instructors shall be thoroughly familiar with all parts of the installation and shall be trained in operating theory as well as practical operation and maintenance work.

Instruction shall be given during the first regular work week after the equipment or system has been accepted and turned over to the Government for regular operation.  The number of man-days (8 hours per day) of instruction furnished shall be as specified in the individual section.  When more than 4 man-days of instruction are specified, use approximately half of the time for classroom instruction.  Use other time for instruction with the equipment or system.

When significant changes or modifications in the equipment or system are made under the terms of the contract, provide additional instruction to acquaint the operating personnel with the changes or modifications.

## 1.8   ACCESSIBILITY OF EQUIPMENT

Install all work so that parts requiring periodic inspection, operation, maintenance, and repair are readily accessible.  Install concealed valves, expansion joints, controls, dampers, and equipment requiring access, in locations freely accessible through access doors.

# PART 2   PRODUCTS

## 2.1   MATERIALS

Materials for various services shall be in accordance with TABLES I and II.  PVC pipe shall contain a minimum of 25 percent recycled content in accordance with ASTM F1760.  Pipe schedules shall be selected based on service requirements.  Pipe fittings shall be compatible with the applicable pipe materials.  Plastic pipe, fittings, and solvent cement shall meet NSF/ANSI 14 and shall be NSF listed for the service intended.  Plastic pipe, fittings, and solvent cement used for potable hot and cold water service shall bear the NSF seal "NSF-PW."  In line devices such as water meters, building valves, check valves, meter stops, valves, fittings and back flow preventers shall comply with PL 93-523 and NSF/ANSI 61, Section 8.  Plastic pipe shall not be installed in air plenums.

### 2.1.1   Pipe Joint Materials

Grooved pipe and hubless cast-iron soil pipe shall not be used underground.  Solder containing lead shall not be used with copper pipe.  Cast iron soil pipe and fittings shall be marked with the collective trademark of the Cast Iron Soil Institute.  Joints and gasket materials shall conform to the following:

a.  Brazing Material:  Brazing material shall conform to AWS A5.8/A5.8M, BCuP-5.

b.  Brazing Flux:  Flux shall be in paste or liquid form appropriate for use with brazing material.  Flux shall be as follows:  lead-free; have a 100 percent flushable residue; contain slightly acidic reagents; contain potassium borides; and contain fluorides.

c.  Solder Material:  Solder metal shall conform to ASTM B32.

d.  Solder Flux:  Flux shall be liquid form, non-corrosive, and conform to ASTM B813, Standard Test 1.

e.  PTFE Tape:  PTFE Tape, for use with Threaded Metal or Plastic Pipe.

f.  Flexible Elastomeric Seals:  ASTM D3139, ASTM D3212 or ASTM F477.

g.  Plastic Solvent Cement for PVC Plastic Pipe:  ASTM D2564 and ASTM D2855.

h.  Press fittings for Copper Pipe and Tube: Copper press fittings shall conform to the material and sizing requirements of ASME B16.18 or ASME B16.22 and performance criteria of IAPMO PS 117.  Sealing elements for copper press fittings shall be EPDM, FKM or HNBR.  Sealing elements shall be factory installed or an alternative supplied fitting manufacturer.  Sealing element shall be selected based on manufacturer's approved application guidelines.

i.  Copper tubing shall conform to ASTM B88, Type K, L or M.

### 2.1.2   Miscellaneous Materials

Miscellaneous materials shall conform to the following:

a.  Copper, Sheet and Strip for Building Construction:  ASTM B370.

b.  Hose Clamps:  SAE J1508.

c.  Supports for Off-The-Floor Plumbing Fixtures:  ASME A112.6.1M.

d.  Gauges - Pressure and Vacuum Indicating Dial Type - Elastic Element:  ASME B40.100.

e.  Thermometers:  ASTM E1.  Mercury shall not be used in thermometers.

### 2.1.3   Pipe Insulation Material

Insulation shall be as specified in Section 23 07 00 THERMAL INSULATION FOR MECHANICAL SYSTEMS.

## 2.2   PIPE HANGERS, INSERTS, AND SUPPORTS

Pipe hangers, inserts, and supports shall conform to MSS SP-58.

## 2.3   VALVES

Valves shall be provided on supplies to equipment and fixtures.  Valves 2-1/2 inches and smaller shall be bronze with threaded bodies for pipe and solder-type connections for tubing.  Valves 3 inches and larger shall have flanged iron bodies and bronze trim.  Pressure ratings shall be based upon the application.  Grooved end valves may be provided if the manufacturer certifies that the valves meet the performance requirements of applicable MSS standard.  Valves shall conform to the following standards:

| Description | Standard |
| --- | --- |
| Butterfly Valves | MSS SP-67 |
| Cast-Iron Gate Valves, Flanged and Threaded Ends | MSS SP-70 |
| Ball Valves with Flanged Butt-Welding Ends for General Service | MSS SP-72 |
| Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends | MSS SP-110 |
| Bronze Gate, Globe, Angle, and Check Valves | MSS SP-80 |
| Water Heater Drain Valves | ASME BPVC SEC IV, Part HLW-810: Requirements for Potable-Water Heaters Bottom Drain Valve |
| Temperature and Pressure Relief Valves for Hot Water Supply Systems | ANSI Z21.22/CSA 4.4 |
| Temperature and Pressure Relief Valves for Automatically Fired Hot Water Boilers | ASME CSD-1 Safety Code No., Part CW, Article 5 |

### 2.3.1   Relief Valves

Water heaters and hot water storage tanks shall have a combination pressure and temperature (P&T) relief valve.  The pressure relief element of a P&T relief valve shall have adequate capacity to prevent excessive pressure buildup in the system when the system is operating at the maximum rate of heat input.  The temperature element of a P&T relief valve shall have a relieving capacity which is at least equal to the total input of the heaters when operating at their maximum capacity.  Relief valves shall be rated according to ANSI Z21.22/CSA 4.4.  Relief valves for systems where the maximum rate of heat input is less than 200,000 Btuh shall have 3/4 inch minimum inlets, and 3/4 inch outlets.  Relief valves for systems where the maximum rate of heat input is greater than 200,000 Btuh shall have 1 inch minimum inlets, and 1 inch outlets.  The discharge pipe from the relief valve shall be the size of the valve outlet.

## 2.4   WATER HEATERS

Water heater types and capacities shall be as indicated.  Each water heater shall have replaceable anodes.  Each primary water heater shall have controls with an adjustable range that includes 90 to 160 degrees F.  Each gas-fired water heater and booster water heater shall have controls with an adjustable range that includes 120 to 180 degrees F.  Hot water systems utilizing recirculation systems shall be tied into building off-hour controls.  The thermal efficiencies and standby heat losses shall conform to TABLE III for each type of water heater specified.  The only exception is that storage water heaters and hot water storage tanks having more than 500 gallons storage capacity need not meet the standard loss requirement if the tank surface area is insulated to R-12.5 and if a standing light is not used.  Plastic materials polyetherimide (PEI) and polyethersulfone (PES) are forbidden to be used for vent piping of combustion gases.  A factory pre-charged expansion tank shall be installed on the cold water supply to each water heater.  Expansion tanks shall be specifically designed for use on potable water systems and shall be rated for 200 degrees F water temperature and 150 psi working pressure.  The expansion tank size and acceptance volume shall be as indicated.

### 2.4.1   Automatic Storage Type

Heaters shall be complete with control system, temperature gauge, and pressure gauge, and shall have ASME rated combination pressure and temperature relief valve.  Automatic storage type heaters must meet the Energy Star product definition specified in

https://www.energystar.gov/products/spec and must be Energy Star certified.

#### 2.4.1.1   Electric Type

Electric type water heaters shall conform to UL 174 with dual heating elements.   Each element shall be 4.5 KW.  The elements shall be wired so that only one element can operate at a time.

## 2.5   PUMPS

### 2.5.1   Circulating Pumps

Domestic hot water circulating pumps shall be electrically driven, single-stage, centrifugal, with mechanical seals, suitable for the intended service.  Pump and motor shall be supported by the piping on which it is installed.  The shaft shall be one-piece, heat-treated, corrosion-resisting steel with impeller and smooth-surfaced housing of bronze.

Motor shall be totally enclosed, fan-cooled and shall have sufficient horsepower for the service required.  Each pump motor shall be equipped with an across-the-line magnetic controller in a NEMA 250, Type 1 enclosure with "START-STOP" switch in cover.

Integral size motors shall be premium efficiency type in accordance with NEMA MG 1.  Pump motors smaller than 1 hp Fractional horsepower pump motors shall have integral thermal overload protection.  Guards shall shield exposed moving parts.

## 2.6   ELECTRICAL WORK

Provide electrical motor driven equipment specified complete with motors, motor starters, and controls as specified herein and in Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM.  Provide internal wiring for components of packaged equipment as an integral part of the equipment.  Provide high efficiency type, single-phase, fractional-horsepower alternating-current motors, including motors that are part of a system, corresponding to the applications in accordance with NEMA MG 11.  In addition to the requirements of Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM, provide polyphase, squirrel-cage medium induction motors with continuous ratings, including motors that are part of a system, that meet the efficiency ratings for premium efficiency motors in accordance with NEMA MG 1.  Provide motors in accordance with NEMA MG 1 and of sufficient size to drive the load at the specified capacity without exceeding the nameplate rating of the motor.

Motors shall be rated for continuous duty with the enclosure specified.   Motor duty requirements shall allow for maximum frequency start-stop operation and minimum encountered interval between start and stop.  Motor torque shall be capable of accelerating the connected load within 20 seconds with 80 percent of the rated voltage maintained at motor terminals during one starting period.  Motor bearings shall be fitted with grease supply fittings and grease relief to outside of the enclosure.

Controllers and contactors shall have auxiliary contacts for use with the controls provided.  Manual or automatic control and protective or signal devices required for the operation specified and any control wiring required for controls and devices specified, but not shown, shall be provided.  For packaged equipment, the manufacturer shall provide controllers, including the required monitors and timed restart.

Power wiring and conduit for field installed equipment shall be provided under and conform to the requirements of Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM.

## 2.7   MISCELLANEOUS PIPING ITEMS

### 2.7.1   Escutcheon Plates

Provide one piece or split hinge metal plates for piping entering floors, walls, and ceilings in exposed spaces.  Provide chromium-plated on copper alloy plates or polished stainless steel finish in finished spaces.  Provide paint finish on plates in unfinished spaces.

### 2.7.2   Pipe Sleeves

Provide where piping passes entirely through walls, ceilings, roofs, and floors.  Sleeves are not required where drain, waste, and vent (DWV) piping passes through concrete floor slabs located on grade, except where penetrating a membrane waterproof floor.

#### 2.7.2.1   Sleeves in Masonry and Concrete

Provide steel pipe sleeves or schedule 40 PVC plastic pipe sleeves.  Sleeves are not required where drain, waste, and vent (DWV) piping passes through concrete floor slabs located on grade.  Core drilling of masonry and concrete may be provided in lieu of pipe sleeves when cavities in the core-drilled hole are completely grouted smooth.

#### 2.7.2.2   Sleeves Not in Masonry and Concrete

Provide 26 gage galvanized steel sheet or PVC plastic pipe sleeves.

### 2.7.3   Pipe Hangers (Supports)

Provide MSS SP-58 Type 1 with adjustable type steel support rods, except as specified or indicated otherwise.  Attach to steel joists with Type 19 or 23 clamps and retaining straps.  Attach to Steel W or S beams with Type 21, 28, 29, or 30 clamps.  Attach to steel angles and vertical web steel channels with Type 20 clamp with beam clamp channel adapter.  Attach to horizontal web steel channel and wood with drilled hole on centerline and double nut and washer.  Attach to concrete with Type 18 insert or drilled expansion anchor.  Provide Type 40 insulation protection shield for insulated piping.

### 2.7.4   Nameplates

Provide 0.125 inch thick melamine laminated plastic nameplates, black matte finish with white center core, for equipment, gages, thermometers, and valves; valves in supplies to faucets will not require nameplates.  Accurately align lettering and engrave minimum of 0.25 inch high normal block lettering into the white core.  Minimum size of nameplates shall be 1.0 by 2.5 inches.  Key nameplates to a chart and schedule for each system. Frame charts and schedules under glass and place where directed near each system.  Furnish two copies of each chart and schedule.

# PART 3   EXECUTION

## 3.1   GENERAL INSTALLATION REQUIREMENTS

Piping located in air plenums shall conform to NFPA 90A requirements.    Piping located in shafts that constitute air ducts or that enclose air ducts shall be noncombustible in accordance with NFPA 90A.  Installation of plastic pipe where in compliance with NFPA may be installed in accordance with PPFA Fire Man.  The plumbing system shall be installed complete with necessary fixtures, fittings, traps, valves, and accessories.  Water and drainage piping shall be extended 5 feet outside the building, unless otherwise indicated.  Piping shall be connected to the exterior service lines or capped or plugged if the exterior service is not in place.  Sewer and water pipes shall be laid in separate trenches, except when otherwise shown.  Valves shall be installed with control no lower than the valve body.

### 3.1.1   Water Pipe, Fittings, and Connections

#### 3.1.1.1   Utilities

The piping shall be extended to fixtures, outlets, and equipment.  The hot-water and cold-water piping system shall be arranged and installed to permit draining.  The supply line to each item of equipment or fixture, except faucets, flush valves, or other control valves which are supplied with integral stops, shall be equipped with a shutoff valve to enable isolation of the item for repair and maintenance without interfering with operation of other equipment or fixtures.  Supply piping to fixtures, faucets, hydrants, shower heads, and flushing devices shall be anchored to prevent movement.

#### 3.1.1.2   Cutting and Repairing

The work shall be carefully laid out in advance, and unnecessary cutting of construction shall be avoided.  Damage to building, piping, wiring, or equipment as a result of cutting shall be repaired by mechanics skilled in the trade involved.

#### 3.1.1.3   Protection of Fixtures, Materials, and Equipment

Pipe openings shall be closed with caps or plugs during installation. Fixtures and equipment shall be tightly covered and protected against dirt, water, chemicals, and mechanical injury.  Upon completion of the work, the fixtures, materials, and equipment shall be thoroughly cleaned, adjusted, and operated.  Safety guards shall be provided for exposed rotating equipment.

#### 3.1.1.4   Mains, Branches, and Runouts

Piping shall be installed as indicated.  Pipe shall be accurately cut and worked into place without springing or forcing.  Structural portions of the building shall not be weakened.  Aboveground piping shall run parallel with the lines of the building, unless otherwise indicated.  Branch pipes from service lines may be taken from top, bottom, or side of main, using crossover fittings required by structural or installation conditions.  Supply pipes, valves, and fittings shall be kept a sufficient distance from other work and other services to permit not less than 1/2 inch between finished covering on the different services.  Bare and insulated water lines shall not bear directly against building structural elements so as to transmit sound to the structure or to prevent flexible movement of the lines.  Water pipe shall not be buried in or under floors unless specifically indicated or approved.  Changes in pipe sizes shall be made with reducing fittings.  Use of bushings will not be permitted except for use in situations in which standard factory fabricated components are furnished to accommodate specific accepted installation practice.  Change in direction shall be made with fittings, except that bending of pipe 4 inches and smaller will be permitted, provided a pipe bender is used and wide sweep bends are formed.  The center-line radius of bends shall be not less than six diameters of the pipe.  Bent pipe showing kinks, wrinkles, flattening, or other malformations will not be acceptable.

#### 3.1.1.5   Pipe Drains

Pipe drains indicated shall consist of 3/4 inch hose bibb with renewable seat and ball valve ahead of hose bibb.  At other low points, 3/4 inch brass plugs or caps shall be provided.  Disconnection of the supply piping at the fixture is an acceptable drain.

#### 3.1.1.6   Expansion and Contraction of Piping

Allowance shall be made throughout for expansion and contraction of water pipe.  Each hot-water and hot-water circulation riser shall have expansion loops or other provisions such as offsets and changes in direction where indicated and required.  Risers shall be securely anchored as required or where indicated to force expansion to loops.  Branch connections from risers shall be made with ample swing or offset to avoid undue strain on fittings or short pipe lengths.  Horizontal runs of pipe over 50 feet in length shall be anchored to the wall or the supporting construction about midway on the run to force expansion, evenly divided, toward the ends.  Sufficient flexibility shall be provided on branch runouts from mains and risers to provide for expansion and contraction of piping.  Flexibility shall be provided by installing one or more turns in the line so that piping will spring enough to allow for expansion without straining.  If mechanical grooved pipe coupling systems are provided, the deviation from design requirements for expansion and contraction may be allowed pending approval of Contracting Officer.

#### 3.1.1.7   Thrust Restraint

Plugs, caps, tees, valves and bends deflecting 11.25 degrees or more, either vertically or horizontally, in waterlines 4 inches in diameter or larger shall be provided with thrust blocks, where indicated, to prevent movement.  Thrust blocking shall be concrete of a mix not leaner than:  1 cement, 2-1/2 sand, 5 gravel; and having a compressive strength of not less than 2000 psi after 28 days.  Blocking shall be placed between solid ground and the fitting to be anchored.  Unless otherwise indicated or directed, the base and thrust bearing sides of the thrust block shall be poured against undisturbed earth.  The side of the thrust block not subject to thrust shall be poured against forms.  The area of bearing will be as shown.  Blocking shall be placed so that the joints of the fitting are accessible for repair.  Steel rods and clamps, protected by galvanizing or by coating with bituminous paint, shall be used to anchor vertical down bends into gravity thrust blocks.

#### 3.1.1.8   Commercial-Type Water Hammer Arresters

Commercial-type water hammer arresters shall be provided on hot- and cold-water supplies and shall be located as generally indicated, with precise location and sizing to be in accordance with PDI WH 201.  Water hammer arresters, where concealed, shall be accessible by means of access doors or removable panels.  Commercial-type water hammer arresters shall conform to ASSE 1010.  Vertical capped pipe columns will not be permitted.

### 3.1.2   Joints

Installation of pipe and fittings shall be made in accordance with the manufacturer's recommendations.  Mitering of joints for elbows and notching of straight runs of pipe for tees will not be permitted.  Joints shall be made up with fittings of compatible material and made for the specific purpose intended.

#### 3.1.2.1   Threaded

Threaded joints shall have American Standard taper pipe threads conforming to ASME B1.20.1.  Only male pipe threads shall be coated with graphite or with an approved graphite compound, or with an inert filler and oil, or shall have a polytetrafluoroethylene tape applied.

#### 3.1.2.2   Mechanical Couplings

Mechanical couplings may be used in conjunction with grooved pipe for aboveground, ferrous or non-ferrous, domestic hot and cold water systems, in lieu of unions, brazed, soldered, welded, flanged, or threaded joints.

Mechanical couplings are permitted in accessible locations including behind access plates.  Flexible grooved joints will not be permitted, except as vibration isolators adjacent to mechanical equipment.  Rigid grooved joints shall incorporate an angle bolt pad design which maintains metal-to-metal contact with equal amount of pad offset of housings upon installation to ensure positive rigid clamping of the pipe.

Designs which can only clamp on the bottom of the groove or which utilize gripping teeth or jaws, or which use misaligned housing bolt holes, or which require a torque wrench or torque specifications will not be permitted.

The Contracting Officer shall be notified 24 hours in advance of test to demonstrate operator's capability, and the test shall be performed at the work site, if practical, or at a site agreed upon.  The operator shall demonstrate the ability to properly adjust the grooving tool, groove the pipe, and to verify the groove dimensions in accordance with the coupling manufacturer's specifications.

#### 3.1.2.3   Unions and Flanges

Unions, flanges and mechanical couplings shall not be concealed in walls, ceilings, or partitions.  Unions shall be used on pipe sizes 2-1/2 inches and smaller; flanges shall be used on pipe sizes 3 inches and larger.

#### 3.1.2.4   Cast Iron Soil, Waste and Vent Pipe

Bell and spigot compression and hubless gasketed clamp joints for soil, waste and vent piping shall be installed per the manufacturer's recommendations.

#### 3.1.2.5   Copper Tube and Pipe

a.  Brazed.  Brazed joints shall be made in conformance with AWS B2.2/B2.2M, ASME B16.50, and CDA A4015 with flux and are acceptable for all pipe sizes.  Copper to copper joints shall include the use of copper-phosphorus or copper-phosphorus-silver brazing metal without flux.  Brazing of dissimilar metals (copper to bronze or brass) shall include the use of flux with either a copper-phosphorus, copper-phosphorus-silver or a silver brazing filler metal.

b.  Soldered.  Soldered joints shall be made with flux and are only acceptable for piping 2 inches and smaller.  Soldered joints shall conform to ASME B31.5 and CDA A4015.  Soldered joints shall not be used in compressed air piping between the air compressor and the receiver.

c.  Copper Tube Extracted Joint.  Mechanically extracted joints shall be made in accordance with ICC IPC.

d.  Press connection.  Copper press connections shall be made in strict accordance with the manufacturer's installation instructions for manufactured rated size.  The joints shall be pressed using the tool(s) approved by the manufacturer of that joint.  Minimum distance between fittings shall be in accordance with the manufacturer's requirements.

#### 3.1.2.6   Plastic Pipe

Acrylonitrile-Butadiene-Styrene (ABS) pipe shall have joints made with solvent cement.  PVC and CPVC pipe shall have joints made with solvent cement elastomeric, threading, (threading of Schedule 80 Pipe is allowed only where required for disconnection and inspection; threading of Schedule 40 Pipe is not allowed), or mated flanged.

### 3.1.3   Dissimilar Pipe Materials

Connections between ferrous and non-ferrous copper water pipe shall be made with dielectric unions or flange waterways.  Dielectric waterways shall have temperature and pressure rating equal to or greater than that specified for the connecting piping.  Waterways shall have metal connections on both ends suited to match connecting piping.  Dielectric waterways shall be internally lined with an insulator specifically designed to prevent current flow between dissimilar metals.  Dielectric flanges shall meet the performance requirements described herein for dielectric waterways.  Connecting joints between plastic and metallic pipe shall be made with transition fitting for the specific purpose.

### 3.1.4   Pipe Sleeves and Flashing

Pipe sleeves shall be furnished and set in their proper and permanent location.

#### 3.1.4.1   Sleeve Requirements

Unless indicated otherwise, provide pipe sleeves meeting the following requirements:

Secure sleeves in position and location during construction.   Provide sleeves of sufficient length to pass through entire thickness of walls, ceilings, roofs, and floors.

A modular mechanical type sealing assembly may be installed in lieu of a waterproofing clamping flange and caulking and sealing of annular space between pipe and sleeve.  The seals shall consist of interlocking synthetic rubber links shaped to continuously fill the annular space between the pipe and sleeve using galvanized steel bolts, nuts, and pressure plates.  The links shall be loosely assembled with bolts to form a continuous rubber belt around the pipe with a pressure plate under each bolt head and each nut.  After the seal assembly is properly positioned in the sleeve, tightening of the bolt shall cause the rubber sealing elements to expand and provide a watertight seal between the pipe and the sleeve.  Each seal assembly shall be sized as recommended by the manufacturer to fit the pipe and sleeve involved.

Sleeves shall not be installed in structural members, except where indicated or approved.  Rectangular and square openings shall be as detailed.  Each sleeve shall extend through its respective floor, or roof, and shall be cut flush with each surface, except for special circumstances. Pipe sleeves passing through floors in wet areas such as mechanical equipment rooms, lavatories, kitchens, and other plumbing fixture areas shall extend a minimum of 4 inches above the finished floor.

Unless otherwise indicated, sleeves shall be of a size to provide a minimum of 1/4 inch clearance between bare pipe or insulation and inside of sleeve or between insulation and inside of sleeve.  Sleeves in bearing walls and concrete slab on grade floors shall be steel pipe or cast-iron pipe.  Sleeves in nonbearing walls or ceilings may be steel pipe, cast-iron pipe, galvanized sheet metal with lock-type longitudinal seam, or plastic.

Except as otherwise specified, the annular space between pipe and sleeve, or between jacket over insulation and sleeve, shall be sealed as indicated with sealants conforming to ASTM C920 and with a primer, backstop material and surface preparation.  The annular space between pipe and sleeve, between bare insulation and sleeve or between jacket over insulation and sleeve shall not be sealed for interior walls which are not designated as fire rated.

Sleeves through below-grade walls in contact with earth shall be recessed 1/2 inch from wall surfaces on both sides.  Annular space between pipe and sleeve shall be filled with backing material and sealants in the joint between the pipe and wall.  Sealant selected for the earth side of the wall shall be compatible with dampproofing/waterproofing materials that are to be applied over the joint sealant.

#### 3.1.4.2   Waterproofing

Waterproofing at floor-mounted water closets shall be accomplished by forming a flashing guard from soft-tempered sheet copper.  The center of the sheet shall be perforated and turned down approximately 1-1/2 inches to fit between the outside diameter of the drainpipe and the inside diameter of the cast-iron or steel pipe sleeve.  The turned-down portion of the flashing guard shall be embedded in sealant to a depth of approximately 1-1/2 inches; then the sealant shall be finished off flush to floor level between the flashing guard and drainpipe.  The flashing guard of sheet copper shall extend not less than 8 inches from the drainpipe and shall be lapped between the floor membrane in a solid coating of bituminous cement.  If cast-iron water closet floor flanges are used, the space between the pipe sleeve and drainpipe shall be sealed with sealant and the flashing guard shall be upturned approximately 1-1/2 inches to fit the outside diameter of the drainpipe and the inside diameter of the water closet floor flange.  The upturned portion of the sheet fitted into the floor flange shall be sealed.

#### 3.1.4.3   Pipe Penetrations of Slab on Grade Floors

Where pipes, fixture drains, floor drains, cleanouts or similar items penetrate slab on grade floors, except at penetrations of floors with waterproofing membrane as specified in paragraphs FLASHING REQUIREMENTS and WATERPROOFING, a groove 1/4 to 1/2 inch wide by 1/4 to 3/8 inch deep shall be formed around the pipe, fitting or drain.  The groove shall be filled with a sealant as specified in Section 07 92 00 JOINT SEALANTS.

#### 3.1.4.4   Pipe Penetrations

Provide sealants for all pipe penetrations.  All pipe penetrations shall be sealed to prevent infiltration of air, insects, and vermin.

### 3.1.5   Fire Seal

Where pipes pass through fire walls, fire-partitions, fire-rated pipe chase walls or floors above grade, a fire seal shall be provided.

### 3.1.6   Supports

#### 3.1.6.1   General

Hangers used to support piping 2 inches and larger shall be fabricated to permit adequate adjustment after erection while still supporting the load.  Pipe guides and anchors shall be installed to keep pipes in accurate alignment, to direct the expansion movement, and to prevent buckling, swaying, and undue strain.  Piping subjected to vertical movement when operating temperatures exceed ambient temperatures shall be supported by variable spring hangers and supports or by constant support hangers.  In the support of multiple pipe runs on a common base member, a clip or clamp shall be used where each pipe crosses the base support member.  Spacing of the base support members shall not exceed the hanger and support spacing required for an individual pipe in the multiple pipe run.  Threaded sections of rods shall not be formed or bent.

#### 3.1.6.2   Pipe Hangers, Inserts, and Supports

Installation of pipe hangers, inserts and supports shall conform to MSS SP-58 except as modified herein.

a.  Types 5, 12, and 26 shall not be used.

b.  Type 3 shall not be used on insulated pipe.

c.  Type 18 inserts shall be secured to concrete forms before concrete is placed.  Continuous inserts which allow more adjustment may be used if they otherwise meet the requirements for type 18 inserts.

d.  Type 19 and 23 C-clamps shall be torqued per MSS SP-58 and shall have both locknuts and retaining devices furnished by the manufacturer.  Field-fabricated C-clamp bodies or retaining devices are not acceptable.

e.  Type 20 attachments used on angles and channels shall be furnished with an added malleable-iron heel plate or adapter.

f.  Type 24 may be used only on trapeze hanger systems or on fabricated frames.

g.  Type 39 saddles shall be used on insulated pipe 4 inches and larger when the temperature of the medium is 60 degrees F or higher.  Type 39 saddles shall be welded to the pipe.

h.  Type 40 shields shall:

(1) Be used on insulated pipe less than 4 inches.

(2) Be used on insulated pipe 4 inches and larger when the temperature of the medium is 60 degrees F or less.

(3) Have a high density insert for all pipe sizes.  High density inserts shall have a density of 8 pcf or greater.

i.  Horizontal pipe supports shall be spaced as specified in MSS SP-58 and a support shall be installed not over 1 foot from the pipe fitting joint at each change in direction of the piping.  Pipe supports shall be spaced not over 5 feet apart at valves.  Operating temperatures in determining hanger spacing for PVC or CPVC pipe shall be 120 degrees F for PVC and 180 degrees F for CPVC.  Horizontal pipe runs shall include allowances for expansion and contraction.

j.  Vertical pipe shall be supported at each floor, except at slab-on-grade, at intervals of not more than 15 feet nor more than 8 feet from end of risers, and at vent terminations.  Vertical pipe risers shall include allowances for expansion and contraction.

k.  Type 35 guides using steel, reinforced polytetrafluoroethylene (PTFE) or graphite slides shall be provided to allow longitudinal pipe movement.  Slide materials shall be suitable for the system operating temperatures, atmospheric conditions, and bearing loads encountered.  Lateral restraints shall be provided as needed.  Where steel slides do not require provisions for lateral restraint the following may be used:

(1) On pipe 4 inches and larger when the temperature of the medium is 60 degrees F or higher, a Type 39 saddle, welded to the pipe, may freely rest on a steel plate.

(2) On pipe less than 4 inches a Type 40 shield, attached to the pipe or insulation, may freely rest on a steel plate.

(3) On pipe 4 inches and larger carrying medium less that 60 degrees F a Type 40 shield, attached to the pipe or insulation, may freely rest on a steel plate.

l.  Pipe hangers on horizontal insulated pipe shall be the size of the outside diameter of the insulation.  The insulation shall be continuous through the hanger on all pipe sizes and applications.

m.  Where there are high system temperatures and welding to piping is not desirable, the type 35 guide shall include a pipe cradle, welded to the guide structure and strapped securely to the pipe.  The pipe shall be separated from the slide material by at least 4 inches or by an amount adequate for the insulation, whichever is greater.

n.  Hangers and supports for plastic pipe shall not compress, distort, cut or abrade the piping, and shall allow free movement of pipe except where otherwise required in the control of expansion/contraction.

#### 3.1.6.3   Structural Attachments

Attachment to building structure concrete and masonry shall be by cast-in concrete inserts, built-in anchors, or masonry anchor devices.  Inserts and anchors shall be applied with a safety factor not less than 5.  Supports shall not be attached to metal decking.  Supports shall not be attached to the underside of concrete filled floor or concrete roof decks unless approved by the Contracting Officer.  Masonry anchors for overhead applications shall be constructed of ferrous materials only.

## 3.2   WATER HEATERS AND HOT WATER STORAGE TANKS

### 3.2.1   Relief Valves

No valves shall be installed between a relief valve and its water heater or storage tank.  The P&T relief valve shall be installed where the valve actuator comes in contact with the hottest water in the heater.  Whenever possible, the relief valve shall be installed directly in a tapping in the tank or heater; otherwise, the P&T valve shall be installed in the hot-water outlet piping.  A vacuum relief valve shall be provided on the cold water supply line to the hot-water storage tank or water heater and mounted above and within 6 inches above the top of the tank or water heater.

### 3.2.2   Heat Traps

Piping to and from each water heater and hot water storage tank shall be routed horizontally and downward a minimum of 2 feet before turning in an upward direction.

### 3.2.3   Connections to Water Heaters

Connections of metallic pipe to water heaters shall be made with dielectric unions or flanges.

### 3.2.4   Expansion Tank

A pre-charged expansion tank shall be installed on the cold water supply between the water heater inlet and the cold water supply shut-off valve.  The Contractor shall adjust the expansion tank air pressure, as recommended by the tank manufacturer, to match incoming water pressure.

### 3.2.5   Domestic Water Heaters

Notify the Contracting Officer when any direct fired domestic water heater over 400,000 BTU/hour is operational and ready to be inspected and certified.

## 3.3   FIXTURES AND FIXTURE TRIMMINGS

### 3.3.1   Access Panels

Access panels shall be provided for concealed valves and controls, or any item requiring inspection or maintenance.  Access panels shall be of sufficient size and located so that the concealed items may be serviced, maintained, or replaced.

### 3.3.2   Traps

Each trap shall be placed as near the fixture as possible, and no fixture shall be double-trapped.  Traps installed on cast-iron soil pipe shall be cast iron.  Traps installed on steel pipe or copper tubing shall be recess-drainage pattern, or brass-tube type.  Traps installed on plastic pipe may be plastic conforming to ASTM D3311.  Traps for acid-resisting waste shall be of the same material as the pipe.

## 3.4   IDENTIFICATION SYSTEMS

### 3.4.1   Identification Tags

Identification tags made of brass, engraved laminated plastic, or engraved anodized aluminum, indicating service and valve number shall be installed on valves, except those valves installed on supplies at plumbing fixtures. Tags shall be 1-3/8 inch minimum diameter, and marking shall be stamped or engraved.  Indentations shall be black, for reading clarity.  Tags shall be attached to valves with No. 12 AWG, copper wire, chrome-plated beaded chain, or plastic straps designed for that purpose.

### 3.4.2   Pipe Color Code Marking

Color code marking of piping shall be as specified in Section 09 90 00 PAINTS AND COATINGS.

### 3.4.3   Color Coding Scheme for Locating Hidden Utility Components

Scheme shall be provided in buildings having suspended grid ceilings.  The color coding scheme shall identify points of access for maintenance and operation of operable components which are not visible from the finished space and installed in the space directly above the suspended grid ceiling. The operable components shall include valves, dampers, switches, linkages and thermostats.  The color coding scheme shall consist of a color code board and colored metal disks.  Each colored metal disk shall be approximately 3/8 inch in diameter and secured to removable ceiling panels with fasteners.  The fasteners shall be inserted into the ceiling panels so that the fasteners will be concealed from view.  The fasteners shall be manually removable without tools and shall not separate from the ceiling panels when panels are dropped from ceiling height.  Installation of colored metal disks shall follow completion of the finished surface on which the disks are to be fastened.  The color code board shall have the approximate dimensions of 3 foot width, 30 inches height, and 1/2 inch thickness.  The board shall be made of wood fiberboard and framed under glass or 1/16 inch transparent plastic cover.  Unless otherwise directed, the color code symbols shall be approximately 3/4 inch in diameter and the related lettering in 1/2 inch high capital letters.  The color code board shall be mounted and located in the mechanical or equipment room.

## 3.5   ESCUTCHEONS

Escutcheons shall be provided at finished surfaces where bare or insulated piping, exposed to view, passes through floors, walls, or ceilings, except in boiler, utility, or equipment rooms.  Escutcheons shall be fastened securely to pipe or pipe covering and shall be satin-finish, corrosion-resisting steel, polished chromium-plated zinc alloy, or polished chromium-plated copper alloy.  Escutcheons shall be either one-piece or split-pattern, held in place by internal spring tension or setscrew.

## 3.6   PAINTING

Painting of pipes, hangers, supports, and other iron work, either in concealed spaces or exposed spaces, is specified in Section 09 90 00 PAINTS AND COATINGS.

### 3.6.1   Painting of New Equipment

New equipment painting shall be factory applied or shop applied, and shall be as specified herein, and provided under each individual section.

#### 3.6.1.1   Factory Painting Systems

Manufacturer's standard factory painting systems may be provided subject to certification that the factory painting system applied will withstand 125 hours in a salt-spray fog test, except that equipment located outdoors shall withstand 500 hours in a salt-spray fog test.  Salt-spray fog test shall be in accordance with ASTM B117, and for that test the acceptance criteria shall be as follows:  immediately after completion of the test, the paint shall show no signs of blistering, wrinkling, or cracking, and no loss of adhesion; and the specimen shall show no signs of rust creepage beyond 0.125 inch on either side of the scratch mark.

The film thickness of the factory painting system applied on the equipment shall not be less than the film thickness used on the test specimen.  If manufacturer's standard factory painting system is being proposed for use on surfaces subject to temperatures above 120 degrees F, the factory painting system shall be designed for the temperature service.

#### 3.6.1.2   Shop Painting Systems for Metal Surfaces

Clean, pretreat, prime and paint metal surfaces; except aluminum surfaces need not be painted.  Apply coatings to clean dry surfaces.  Clean the surfaces to remove dust, dirt, rust, oil and grease by wire brushing and solvent degreasing prior to application of paint, except metal surfaces subject to temperatures in excess of 120 degrees F shall be cleaned to bare metal.

Where more than one coat of paint is specified, apply the second coat after the preceding coat is thoroughly dry.  Lightly sand damaged painting and retouch before applying the succeeding coat. Color of finish coat shall be aluminum or light gray.

a.  Temperatures Less Than 120 Degrees F: Immediately after cleaning, the metal surfaces subject to temperatures less than 120 degrees F shall receive one coat of pretreatment primer applied to a minimum dry film thickness of 0.3 mil, one coat of primer applied to a minimum dry film thickness of one mil; and two coats of enamel applied to a minimum dry film thickness of one mil per coat.

b.  Temperatures Between 120 and 400 Degrees F:  Metal surfaces subject to temperatures between 120 and 400 degrees F shall receive two coats of 400 degrees F heat-resisting enamel applied to a total minimum thickness of 2 mils.

c.  Temperatures Greater Than 400 Degrees F: Metal surfaces subject to temperatures greater than 400 degrees F shall receive two coats of 600 degrees F heat-resisting paint applied to a total minimum dry film thickness of 2 mils.

## 3.7   TESTS, FLUSHING AND DISINFECTION

### 3.7.1   Plumbing System

The following tests shall be performed on the plumbing system in accordance with ICC IPC, except that the drainage and vent system final test shall include the smoke test.  The Contractor has the option to perform a peppermint test in lieu of the smoke test.  If a peppermint test is chosen, the Contractor must submit a testing procedure and reasons for choosing this option in lieu of the smoke test to the Contracting Officer for approval.

a.  Water Supply Systems Tests.

### 3.7.2   Defective Work

If inspection or test shows defects, such defective work or material shall be replaced or repaired as necessary and inspection and tests shall be repeated.  Repairs to piping shall be made with new materials.  Caulking of screwed joints or holes will not be acceptable.

### 3.7.3   System Flushing

#### 3.7.3.1   During Flushing

Before operational tests or disinfection, potable water piping system shall be flushed with potable water.  Sufficient water shall be used to produce a water velocity that is capable of entraining and removing debris in all portions of the piping system.  This requires simultaneous operation of all fixtures on a common branch or main in order to produce a flushing velocity of approximately 4 fps through all portions of the piping system.  In the event that this is impossible due to size of system, the Contracting Officer (or the designated representative) shall specify the number of fixtures to be operated during flushing.  Contractor shall provide adequate personnel to monitor the flushing operation and to ensure that drain lines are unobstructed in order to prevent flooding of the facility.  Contractor shall be responsible for any flood damage resulting from flushing of the system.  Flushing shall be continued until entrained dirt and other foreign materials have been removed and until discharge water shows no discoloration.  All faucets and drinking water fountains, to include any device considered as an end point device by NSF/ANSI 61, Section 9, shall be flushed a minimum of 0.25 gallons per 24 hour period, ten times over a 14 day period.

#### 3.7.3.2   After Flushing

System shall be drained at low points.  Strainer screens shall be removed, cleaned, and replaced.  After flushing and cleaning, systems shall be prepared for testing by immediately filling water piping with clean, fresh potable water.  Any stoppage, discoloration, or other damage to the finish, furnishings, or parts of the building due to the Contractor's failure to properly clean the piping system shall be repaired by the Contractor.  When the system flushing is complete, the hot-water system shall be adjusted for uniform circulation.  Flushing devices and automatic control systems shall be adjusted for proper operation according to manufacturer's instructions.  Comply with ASHRAE 90.1 - IP for minimum efficiency requirements.  Unless more stringent local requirements exist, lead levels shall not exceed limits established by 40 CFR 141.80 (c)(1).  The water supply to the building shall be tested separately to ensure that any lead contamination found during potable water system testing is due to work being performed inside the building.

### 3.7.4   Operational Test

Upon completion of flushing and prior to disinfection procedures, the Contractor shall subject the plumbing system to operating tests to demonstrate satisfactory installation, connections, adjustments, and functional and operational efficiency.  Such operating tests shall cover a period of not less than 8 hours for each system and shall include the following information in a report with conclusion as to the adequacy of the system:

a.  Time, date, and duration of test.

b.  Water pressures at the most remote and the highest fixtures.

c.  Operation of each fixture and fixture trim.

d.  Operation of each valve, hydrant, and faucet.

e.  Pump suction and discharge pressures.

f.  Temperature of each domestic hot-water supply.

g.  Operation of each floor and roof drain by flooding with water.

h.  Operation of each vacuum breaker and backflow preventer.

i.  Complete operation of each water pressure booster system, including pump start pressure and stop pressure.

j.  Compressed air readings at each compressor and at each outlet. Each indicating instrument shall be read at 1/2 hour intervals.  The report of the test shall be submitted in quadruplicate.  The Contractor shall furnish instruments, equipment, and personnel required for the tests; the Government will furnish the necessary water and electricity.

### 3.7.5   Disinfection

After all system components are provided and operational tests are complete, the entire domestic hot- and cold-water distribution system shall be disinfected.  Before introducing disinfecting chlorination material, entire system shall be flushed with potable water until any entrained dirt and other foreign materials have been removed.

Water chlorination procedure shall be in accordance with AWWA C651 and AWWA C652 as modified and supplemented by this specification.  The chlorinating material shall be hypochlorites or liquid chlorine. The chlorinating material shall be fed into the water piping system at a constant rate at a concentration of at least 50 parts per million (ppm).  Feed a properly adjusted hypochlorite solution injected into the system with a hypochlorinator, or inject liquid chlorine into the system through a solution-feed chlorinator and booster pump until the entire system is completely filled.

Test the chlorine residual level in the water at 6 hour intervals for a continuous period of 24 hours. If at the end of a 6 hour interval, the chlorine residual has dropped to less than 25 ppm, flush the piping including tanks with potable water, and repeat the above chlorination procedures.  During the chlorination period, each valve and faucet shall be opened and closed several times.

After the second 24 hour period, verify that no less than 25 ppm chlorine residual remains in the treated system. The 24 hour chlorination procedure must be repeated until no less than 25 ppm chlorine residual remains in the treated system.

Upon the specified verification, the system including tanks shall then be flushed with potable water until the residual chlorine level is reduced to less than one part per million.  During the flushing period, each valve and faucet shall be opened and closed several times.

Take additional samples of water in disinfected containers, for bacterial examination, at locations specified by the Contracting Officer.  Test these samples for total coliform organisms (coliform bacteria, fecal coliform, streptococcal, and other bacteria) in accordance with EPA SM 9223.  The testing method used shall be EPA approved for drinking water systems and shall comply with applicable local and state requirements.

Disinfection shall be repeated until bacterial tests indicate the absence of coliform organisms (zero mean coliform density per 100 milliliters) in the samples for at least 2 full days.  The system will not be accepted until satisfactory bacteriological results have been obtained.

## 3.8   PERFORMANCE OF WATER HEATING EQUIPMENT

Standard rating condition terms are as follows:

EF = Energy factor, minimum overall efficiency.

ET = Minimum thermal efficiency with 70 degrees F delta T.

SL = Standby loss is maximum (Btu/h) based on a 70 degrees F temperature difference between stored water and ambient requirements.

V = Rated volume in gallons

Q = Nameplate input rate in kW (Btu/h)

### 3.8.1   Storage Water Heaters

#### 3.8.1.1   Electric

a.  Storage capacity of 60 gallons shall have a minimum energy factor (EF) of 0.93 or higher per FEMP requirements.

b.  Storage capacity of 60 gallons or more shall have a minimum energy factor (EF) of 0.91 or higher per FEMP requirements.

## 3.9   TABLES

| TABLE I |
| --- |
| PIPE AND FITTING MATERIALS FOR DRAINAGE, WASTE, VENT AND CONDENSATE DRAIN PIPING SYSTEMS |
| Item # | Pipe and Fitting Materials | SERVICE A |
| 1 | Cast copper alloy solder joint pressure fittings, ASME B16.18for use with Item 14 | X |
| 2 | Seamless copper pipe, ASTM B42 | X |
| 3 | Copper drainage tube, (DWV), ASTM B306 | X |
| 4 | Polyvinyl Chloride plastic drain, waste and vent pipe and fittings, ASTM D2665, ASTM F891, (Sch 40) ASTM F1760 | X |
| SERVICE: A - Condensate Drain Aboveground |

| TABLE II |
| --- |
| PIPE AND FITTING MATERIALS FOR PRESSURE PIPING SYSTEMS |
| Item # | Pipe and Fitting Materials | SERVICE A | SERVICE B |
| 1 | Wrought copper and bronze solder-joint pressure fittings, ASME B16.22 for use with Items 5, 7 and 8 | X | X |
| 2 | Cast copper alloy solder-joint pressure fittings, ASME B16.18 for use with Item 8 | X | X |
| 3 | Fittings: brass or bronze; ASME B16.15, and ASME B16.18 ASTM B828 | X | X |
| 4 | Press Fittings | X | X |
|  | SERVICE: A - Cold Water Service Aboveground B - Hot and Cold Water Distribution 180 degrees F Maximum Aboveground Indicated types are minimum wall thicknesses. ** - Type L - Hard *** - Type K - Hard temper with brazed joints only or type K-soft temper without joints in or under floors **** - In or under slab floors only brazed joints |

| TABLE III |
| --- |
| STANDARD RATING CONDITIONS AND MINIMUM PERFORMANCE RATINGS FOR WATER HEATING EQUIPMENT |
| FUEL | STORAGE CAPACITY GALLONS | INPUT RATING | TEST PROCEDURE | REQUIRED PERFORMANCE |
| A. STORAGE WATER HEATERS |
| Elect. | 60 max. |  | 10 CFR 430 | EF = 0.93 |
| Elect. | 60 min. |  | 10 CFR 430 | EF = 0.91 |
| Elect. | 20 min. | 12 kW max. | 10 CFR 430 | EF = 0.93-0.00132V minimum |
| Elect. | 20 min. | 12 kW max. | ANSI Z21.10.3/CSA 4.3 (Addenda B) | SL = 20+35x(V^^1/2) maximum |
| TERMS: EF = Energy factor, minimum overall efficiency. ET = Minimum thermal efficiency with 70 degrees F delta T. SL = Standby loss is maximum Btu/h based on a 70 degree F temperature difference between stored water and ambient requirements. V = Rated storage volume in gallons Q = Nameplate input rate in Btu/h |

-- End of Section --

SECTION 23 00 00

AIR SUPPLY, DISTRIBUTION, VENTILATION, AND EXHAUST SYSTEMS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING ENGINEERS (ASHRAE)

ASHRAE 62.1	(2010; Errata 2011; INT 3 2012; INT 4 2012; INT 5 2013) Ventilation for Acceptable Indoor Air Quality

ASHRAE 70	(2006; R 2011) Method of Testing for Rating the Performance of Air Outlets and Inlets

ASTM INTERNATIONAL (ASTM)

ASTM A123/A123M	(2013) Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products

ASTM A53/A53M	(2012) Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless

ASTM A924/A924M	(2016) Standard Specification for General Requirements for Steel Sheet, Metallic-Coated by the Hot-Dip Process

ASTM B117	(2016) Standard Practice for Operating Salt Spray (Fog) Apparatus

ASTM B766	(1986; R 2008) Standard Specification for Electrodeposited Coatings of Cadmium

ASTM C553	(2013) Standard Specification for Mineral Fiber Blanket Thermal Insulation for Commercial and Industrial Applications

ASTM D1654	(2008) Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

ASTM D3359	(2009; E 2010; R 2010) Measuring Adhesion by Tape Test

ASTM D520	(2000; R 2011) Zinc Dust Pigment

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

NEMA MG 1	(2016) Motors and Generators

U.S. DEPARTMENT OF ENERGY (DOE)

PL-109-58	(1992; R 2005) Energy Efficient Procurement Requirements

U.S. NATIONAL ARCHIVES AND RECORDS ADMINISTRATION (NARA)

40 CFR 82	Protection of Stratospheric Ozone

UNDERWRITERS LABORATORIES (UL)

UL 6	(2007; Reprint Nov 2014) Electrical Rigid Metal Conduit-Steel

UL Bld Mat Dir	(2012) Building Materials Directory

## 1.2   SYSTEM DESCRIPTION

Furnish ductwork, piping offsets, fittings, and accessories as required to provide a complete installation.  Coordinate the work of the different trades to avoid interference between piping, equipment, structural, and electrical work.  Provide complete, in place, all necessary offsets in piping and ductwork, and all fittings, and other components, required to install the work as indicated and specified.

### 1.2.1   Mechanical Equipment Identification

The number of charts and diagrams shall be equal to or greater than the number of mechanical equipment rooms.  Where more than one chart or diagram per space is required, mount these in edge pivoted, swinging leaf, extruded aluminum frame holders which open to 170 degrees.

#### 1.2.1.1   Charts

Provide chart listing of equipment by designation numbers and capacities such as flow rates, pressure and temperature differences, heating and cooling capacities, horsepower, pipe sizes, and voltage and current characteristics.

#### 1.2.1.2   Diagrams

Submit proposed diagrams, at least 2 weeks prior to start of related testing.  Provide neat mechanical drawings provided with extruded aluminum frame under 1/8-inch glass or laminated plastic, system diagrams that show the layout of equipment, piping, and ductwork, and typed condensed operation manuals explaining preventative maintenance procedures, methods of checking the system for normal, safe operation, and procedures for safely starting and stopping the system.  After approval, post these items where directed.

### 1.2.2   Service Labeling

Label equipment, including fans, air handlers, terminal units, etc. with labels made of self-sticking, plastic film designed for permanent installation.  Labels shall be in accordance with the typical examples below:

| SERVICE | LABEL AND TAG DESIGNATION |
| --- | --- |
| Air Cooled Condensing Units | DCU-3 |
| Air Handling Units | AHU-1 |
| Energy Recovery Ventilator Units | ERU-1 |

Identify similar services with different temperatures or pressures.  Where pressures could exceed 125 pounds per square inch, gage, include the maximum system pressure in the label.  Label and arrow piping in accordance with the following:

a.  Each point of entry and exit of pipe passing through walls.

b.  Each change in direction, i.e., elbows, tees.

c.  In congested or hidden areas and at all access panels at each point required to clarify service or indicated hazard.

## 1.3   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-02 Shop Drawings

Detail Drawings

SD-03 Product Data

Diffusers, Registers, and Grilles

Test Procedures

Diagrams

Air Cooled Condensing Units

Air Handling Units

Energy Recovery Ventilator Units

SD-07 Certificates

Bolts

Ozone Depleting Substances

Proof Of Technician Certification

Proof Of Equipment Certification For Recovery Or Recycling Equipment

Proof Of Availability Of Certified Recovery Or Recycling Equipment

SD-08 Manufacturer's Instructions

Manufacturer's Installation Instructions

Operation and Maintenance Training

SD-10 Operation and Maintenance Data

Operation and Maintenance Manuals

Air Cooled Condensing Units

Air Handling Units

Energy Recovery Ventilator Units

## 1.4   QUALITY ASSURANCE

Except as otherwise specified, approval of materials and equipment is based on manufacturer's published data.

a.  Where materials and equipment are specified to conform to the standards of the Underwriters Laboratories, the label of or listing with reexamination in UL Bld Mat Dir, and UL 6 is acceptable as sufficient evidence that the items conform to Underwriters Laboratories requirements.  In lieu of such label or listing, submit a written certificate from any nationally recognized testing agency, adequately equipped and competent to perform such services, stating that the items have been tested and that the units conform to the specified requirements.  Outline methods of testing used by the specified agencies.

b.  Where materials or equipment are specified to be constructed or tested, or both, in accordance with the standards of the ASTM International (ASTM), the ASME International (ASME), or other standards, a manufacturer's certificate of compliance of each item is acceptable as proof of compliance.

c.  Conformance to such agency requirements does not relieve the item from compliance with other requirements of these specifications.

d.  Where products are specified to meet or exceed the specified energy efficiency requirement of FEMP-designated or ENERGY STAR covered product categories, equipment selected shall have as a minimum the efficiency rating identified under "Energy-Efficient Products" at http://www1.eere.energy.gov/femp/procurement.

These specifications conform to the efficiency requirements as defined in Public Law PL-109-58, "Energy Policy Act of 2005" for federal procurement of energy-efficient products.  Equipment having a lower efficiency than ENERGY STAR or FEMP requirements may be specified if the designer determines the equipment to be more life-cycle cost effective using the life-cycle cost analysis methodology and procedure in 10 CFR 436.

### 1.4.1   Prevention of Corrosion

Protect metallic materials against corrosion.  Manufacturer shall provide rust-inhibiting treatment and standard finish for the equipment enclosures.  Do not use aluminum in contact with earth, and where connected to dissimilar metal.  Protect aluminum by approved fittings, barrier material, or treatment.  Ferrous parts such as anchors, bolts, braces, boxes, bodies, clamps, fittings, guards, nuts, pins, rods, shims, thimbles, washers, and miscellaneous parts not of corrosion-resistant steel or nonferrous materials shall be hot-dip galvanized in accordance with ASTM A123/A123M for exterior locations and cadmium-plated in conformance with ASTM B766 for interior locations.

### 1.4.2   Asbestos Prohibition

Do not use asbestos and asbestos-containing products.

### 1.4.3   Ozone Depleting Substances Used as Refrigerants

Minimize releases of Ozone Depleting Substances (ODS) during repair, maintenance, servicing or disposal of appliances containing ODS's by complying with all applicable sections of 40 CFR 82 Part 82 Subpart F.  Any person conducting repair, maintenance, servicing or disposal of appliances shall comply with the following:

1.  Do not knowingly vent or otherwise release into the environment, Class I or Class II substances used as a refrigerant.

2.  Do not open appliances without meeting the requirements of 40 CFR 82 Part 82.156 Subpart F, regarding required practices for evacuation and collection of refrigerant and 40 CFR 82 Part 82.158 Subpart F, regarding standards of recycling and recovery equipment.

3.  Only persons who comply with 40 CFR 82 Part 82.161 Subpart F, regarding technician certification, can conduct work on appliances containing refrigerant.

In addition, provide copies of all applicable certifications at least 14 calendar days prior to initiating maintenance, repair, servicing, dismantling or disposal of appliances, including:

#### 1.4.3.1   Proof of Technician Certification

#### 1.4.3.2   Proof of Equipment Certification for recovery or recycling equipment.

#### 1.4.3.3   Proof of availability of certified recovery or recycling equipment.

### 1.4.4   Use of Ozone Depleting Substances, Other than Refrigerants

The use of Class I or Class II ODS's listed as nonessential in 40 CFR 82 Part 82.66 Subpart C is prohibited.  These prohibited materials and uses include:

a.  Any plastic party spray streamer or noise horn which is propelled by a chlorofluorocarbon

b.  Any cleaning fluid for electronic and photographic equipment which contains a chlorofluorocarbon; including liquid packaging, solvent wipes, solvent sprays, and gas sprays.

c.  Any plastic flexible or packaging foam product which is manufactured with or contains a chlorofluorocarbon, including, open cell foam, open cell rigid polyurethane poured foam, closed cell extruded polystyrene sheet foam, closed cell polyethylene foam and closed cell polypropylene foam except for flexible or packaging foam used in coaxial cabling.

d.  Any aerosol product or other pressurized dispenser which contains a chlorofluorocarbon, except for those listed in 40 CFR 82 Part 82.66 Subpart C.

Request a waiver if a facility requirement dictates that a prohibited material is necessary to achieve project goals.  Submit the waiver request in writing to the Contracting Officer.  The waiver will be evaluated and dispositioned.

### 1.4.5   Detail Drawings

Submit detail drawings showing equipment layout, including assembly and installation details and electrical connection diagrams; ductwork layout showing the location of all supports and hangers, typical hanger details, gauge reinforcement, reinforcement spacing rigidity classification, and static pressure and seal classifications.  Include any information required to demonstrate that the system has been coordinated and functions properly as a unit on the drawings and show equipment relationship to other parts of the work, including clearances required for operation and maintenance.  Submit drawings showing bolt-setting information, and foundation bolts prior to concrete foundation construction for all equipment indicated or required to have concrete foundations.  Submit function designation of the equipment and any other requirements specified throughout this Section with the shop drawings.

### 1.4.6   Test Procedures

Submit proposed test procedures and test schedules for the ductwork leak test, and performance tests of systems, at least 2 weeks prior to the start of related testing.

## 1.5   DELIVERY, STORAGE, AND HANDLING

Protect stored equipment at the jobsite from the weather, humidity and temperature variations, dirt and dust, or other contaminants.  Additionally, cap or plug all pipes until installed.

# PART 2   PRODUCTS

## 2.1   STANDARD PRODUCTS

Except for the fabricated duct, plenums and casings specified in paragraphs "Metal Ductwork" and "Plenums and Casings for Field-Fabricated Units", provide components and equipment that are standard products of  manufacturers regularly engaged in the manufacturing of products that are of a similar material, design and workmanship.  This requirement applies to all equipment, including diffusers, registers, fire dampers, and balancing dampers.

a.  Standard products are defined as components and equipment that have been in satisfactory commercial or industrial use in similar applications of  similar size for at least two years before bid opening.

b.  Prior to this two year period, these standard products shall have been sold on the commercial market using advertisements in  manufacturers' catalogs or brochures.   These manufacturers' catalogs, or brochures shall have been copyrighted documents or have been identified with a manufacturer's document number.

c.  Provide equipment items that are supported by a service organization.  In product categories covered by ENERGY STAR or the Federal Energy Management Program, provide equipment that is listed on the ENERGY STAR Qualified Products List or that meets or exceeds the FEMP-designated Efficiency Requirements.

## 2.2   IDENTIFICATION PLATES

In addition to standard manufacturer's identification plates, provide engraved laminated phenolic identification plates for each piece of mechanical equipment.  Identification plates are to designate the function of the equipment.  Submit designation with the shop drawings.  Identification plates shall be three layers, black-white-black, engraved to show white letters on black background.  Letters shall be upper case.  Identification plates 1-1/2-inches high and smaller shall be 1/16-inch thick, with engraved lettering 1/8-inch high; identification plates larger than 1-1/2-inches high shall be 1/8-inch thick, with engraved lettering of suitable height.  Identification plates 1-1/2-inches high and larger shall have beveled edges.  Install identification plates using a compatible adhesive.

## 2.3   EQUIPMENT GUARDS AND ACCESS

Fully enclose or guard belts, pulleys, chains, gears, couplings, projecting setscrews, keys, and other rotating parts exposed to personnel contact according to OSHA requirements.  Properly guard or cover with insulation of a type specified, high temperature equipment and piping exposed to contact by personnel or where it creates a potential fire hazard.

## 2.4   ELECTRICAL WORK

a.  Provide motors, controllers, integral disconnects, contactors, and controls with their respective pieces of equipment, except controllers indicated as part of motor control centers.  Provide electrical equipment, including motors and wiring, as specified in Section 26 20 00INTERIOR DISTRIBUTION SYSTEM.  Provide manual or automatic control and protective or signal devices required for the operation specified and control wiring required for controls and devices specified, but not shown.  For packaged equipment, include manufacturer provided controllers with the required monitors and timed restart.

b.  Provide motors in accordance with NEMA MG 1 and of sufficient size to drive the load at the specified capacity without exceeding the nameplate rating of the motor.  Provide motors rated for continuous duty with the enclosure specified.  Provide motor duty that allows for maximum frequency start-stop operation and minimum encountered interval between start and stop.  Provide motor torque capable of accelerating the connected load within 20 seconds with 80 percent of the rated voltage maintained at motor terminals during one starting period.  Provide motor starters complete with thermal overload protection and other necessary appurtenances.  Fit motor bearings with grease supply fittings and grease relief to outside of the enclosure.

## 2.5   ANCHOR BOLTS

Provide anchor bolts for equipment placed on concrete equipment pads or on concrete slabs.  Bolts to be of the size and number recommended by the equipment manufacturer and located by means of suitable templates.  Installation of anchor bolts shall not degrade the surrounding concrete.

## 2.6   PAINTING

Paint equipment units in accordance with approved equipment manufacturer's standards unless specified otherwise.  Field retouch only if approved.  Otherwise, return equipment to the factory for refinishing.

## 2.7   INDOOR AIR QUALITY

Provide equipment and components that comply with the requirements of ASHRAE 62.1 unless more stringent requirements are specified herein.

## 2.8   DUCT SYSTEMS

### 2.8.1   Diffusers, Registers, and Grilles

Provide factory-fabricated units of corrosion-resistant steel or aluminum that distributes the specified quantity of air evenly over space intended without causing noticeable drafts, air movement faster than 50 fpm in occupied zone, or dead spots anywhere in the conditioned area.  Provide outlets for diffusion, spread, throw, and noise level as required for specified performance.  Certify performance according to ASHRAE 70.  Provide sound rated and certified inlets and outlets according to ASHRAE 70.  Provide sound power level as indicated.  Provide diffusers and registers with volume damper with accessible operator, unless otherwise indicated; or if standard with the manufacturer, an automatically controlled device is acceptable.  Provide opposed blade type volume dampers for all diffusers and registers.

## 2.9   FACTORY PAINTING

Factory paint new equipment, which are not of galvanized construction.  Paint with a corrosion resisting paint finish according to ASTM A123/A123M or ASTM A924/A924M.  Clean, phosphatize and coat internal and external ferrous metal surfaces with a paint finish which has been tested according to ASTM B117, ASTM D1654, and ASTM D3359.  Submit evidence of satisfactory paint performance for a minimum of 125 hours for units to be installed indoors and 500 hours for units to be installed outdoors.  Provide rating of failure at the scribe mark that is not less than 6, average creepage not greater than 1/8 inch.  Provide rating of the inscribed area that is not less than 10, no failure.  On units constructed of galvanized steel that have been welded, provide a final shop docket of zinc-rich protective paint on exterior surfaces of welds or welds that have burned through from the interior according to ASTM D520 Type I.

## 2.10   SUPPLEMENTAL COMPONENTS/SERVICES

### 2.10.1   Insulation

The requirements for shop and field applied insulation are specified in Section 23 07 00 THERMAL INSULATION FOR MECHANICAL SYSTEMS.

### 2.10.2   Controls

The requirements for controls are specified in Section 23 05 93 TESTING, ADJUSTING, AND BALANCING OF HVAC SYSTEMS.

# PART 3   EXECUTION

## 3.1   EXAMINATION

After becoming familiar with all details of the work, verify all dimensions in the field, and advise the Contracting Officer and Contracting Officer's Representative of any discrepancy before performing the work.

## 3.2   INSTALLATION

a.  Install materials and equipment in accordance with the requirements of the contract drawings and approved manufacturer's installation instructions.  Accomplish installation by workers skilled in this type of work.  Perform installation so that there is no degradation of the designed fire ratings of walls, partitions, ceilings, and floors.

b.  No installation is permitted to block or otherwise impede access to any existing machine or system.  Install all hinged doors to swing open a minimum of 120 degrees.  Provide an area in front of all access doors that clears a minimum of 3 feet.  In front of all access doors to electrical circuits, clear the area the minimum distance to energized circuits as specified in OSHA Standards, part 1910.333 (Electrical-Safety Related work practices)and an additional 3 feet.

### 3.2.1   Condensate Drain Lines

Provide water seals in the condensate drain from all units.  Provide a depth of each seal of 2 inches plus the number of inches, measured in water gauge, of the total static pressure rating of the unit to which the drain is connected.  Provide water seals that are constructed of 2 tees and an appropriate U-bend with the open end of each tee plugged.  Provide pipe cap or plug cleanouts where indicated.  Connect drains indicated to connect to the sanitary waste system using an indirect waste fitting.

### 3.2.2   Equipment and Installation

Provide frames and supports for air handling units, fans, coils, dampers, and other similar items requiring supports.  Floor mount or ceiling hang air handling units as indicated.  Anchor and fasten as detailed.  Set floor-mounted equipment on not less than 4 inch concrete pads or curbs doweled in place unless otherwise indicated.  Make concrete foundations heavy enough to minimize the intensity of the vibrations transmitted to the piping, duct work and the surrounding structure, as recommended in writing by the equipment manufacturer.  Make the concrete foundation a mass not less than three times the weight of the components to be supported.

### 3.2.3   Access Panels

Install access panels for concealed valves, vents, controls, dampers, and items requiring inspection or maintenance of sufficient size, and locate them so that the concealed items are easily serviced and maintained or completely removed and replaced.

### 3.2.4   Insulation

Provide thickness and application of insulation materials for ductwork, piping, and equipment according to Section 23 07 00 THERMAL INSULATION FOR MECHANICAL SYSTEMS.  Externally insulate outdoor air intake ducts and plenums up to the point where the outdoor air reaches the conditioning unit.

### 3.2.5   Duct Test Holes

Provide holes with closures or threaded holes with plugs in ducts and plenums as indicated or where necessary for the use of pitot tube in balancing the air system.  Plug insulated duct at the duct surface, patched over with insulation and then marked to indicate location of test hole if needed for future use.

## 3.3   EQUIPMENT PADS

Provide equipment pads to the dimensions shown or, if not shown, to conform to the shape of each piece of equipment served with a minimum 3-inch margin around the equipment and supports.  Allow equipment bases and foundations, when constructed of concrete or grout, to cure a minimum of 14 calendar days before being loaded.

## 3.4   CUTTING AND PATCHING

Install work in such a manner and at such time that a minimum of cutting and patching of the building structure is required.  Make holes in exposed locations, in or through existing floors, by drilling and smooth by sanding.  Use of a jackhammer is permitted only where specifically approved.  Make holes through masonry walls to accommodate sleeves with an iron pipe masonry core saw.

## 3.5   CLEANING

Thoroughly clean surfaces of piping and equipment that have become covered with dirt, plaster, or other material during handling and construction before such surfaces are prepared for final finish painting or are enclosed within the building structure.  Before final acceptance, clean mechanical equipment, including piping, ducting, and fixtures, and free from dirt, grease, and finger marks.  When the work area is in an occupied space such as office, protect all furniture and equipment from dirt and debris.  Incorporate housekeeping for field construction work which leaves all furniture and equipment in the affected area free of construction generated dust and debris; and, all floor surfaces vacuum-swept clean.

## 3.6   PENETRATIONS

Provide sleeves and prepared openings for duct mains, branches, and other penetrating items, and install during the construction of the surface to be penetrated.  Cut sleeves flush with each surface.  Place sleeves for round duct 15 inches and smaller.  Build framed, prepared openings for round duct larger than 15 inches and square, rectangular or oval ducts.  Sleeves and framed openings are also required where grilles, registers, and diffusers are installed at the openings.  Provide one inch clearance between penetrating and penetrated surfaces except at grilles, registers, and diffusers.  Pack spaces between sleeve or opening and duct or duct insulation with mineral fiber conforming with ASTM C553, Type 1, Class B-2.

### 3.6.1   Sleeves

Fabricate sleeves, except as otherwise specified or indicated, from 20 gauge thick mill galvanized sheet metal.  Where sleeves are installed in bearing walls or partitions, provide black steel pipe conforming with ASTM A53/A53M, Schedule 20.

### 3.6.2   Framed Prepared Openings

Fabricate framed prepared openings from 20 gauge galvanized steel, unless otherwise indicated.

### 3.6.3   Insulation

Provide duct insulation in accordance with Section 23 07 00 THERMAL INSULATION FOR MECHANICAL SYSTEMS continuous through sleeves and prepared openings except firewall penetrations.  Terminate duct insulation at fire dampers and flexible connections.  For duct handling air at or below 60 degrees F, provide insulation continuous over the damper collar and retaining angle of fire dampers, which are exposed to unconditioned air.

### 3.6.4   Closure Collars

Provide closure collars of a minimum 4 inches wide, unless otherwise indicated, for exposed ducts and items on each side of penetrated surface, except where equipment is installed.  Install collar tight against the surface and fit snugly around the duct or insulation.  Grind sharp edges smooth to prevent damage to penetrating surface.  Fabricate collars for round ducts 15 inches in diameter or less from 20 gauge galvanized steel.  Fabricate collars for square and rectangular ducts, or round ducts with minimum dimension over 15 inches from 18 gauge galvanized steel.  Fabricate collars for square and rectangular ducts with a maximum side of 15 inches or less from 20 gauge galvanized steel.  Install collars with fasteners a maximum of 6 inches on center.  Attach to collars a minimum of 4 fasteners where the opening is 12 inches in diameter or less, and a minimum of 8 fasteners where the opening is 20 inches in diameter or less.

## 3.7   TESTING, ADJUSTING, AND BALANCING

The requirements for testing, adjusting, and balancing are specified in Section 23 05 93 TESTING, ADJUSTING AND BALANCING FOR HVAC.  Begin testing, adjusting, and balancing only when the air supply and distribution, including controls, has been completed, with the exception of performance tests.

## 3.8   CLEANING AND ADJUSTING

Provide a temporary bypass for water coils to prevent flushing water from passing through coils.  Inside of air terminal units, thoroughly clean ducts, plenums, and casing of debris and blow free of small particles of rubbish and dust and then vacuum clean before installing outlet faces.  Wipe equipment clean, with no traces of oil, dust, dirt, or paint spots.  Provide temporary filters prior to startup of all fans that are operated during construction, and install new filters after all construction dirt has been removed from the building, and the ducts, plenums, casings, and other items specified have been vacuum cleaned.  Maintain system in this clean condition until final acceptance.  Properly lubricate bearings with oil or grease as recommended by the manufacturer.  Tighten belts to proper tension.  Adjust control valves and other miscellaneous equipment requiring adjustment to setting indicated or directed.  Adjust fans to the speed indicated by the manufacturer to meet specified conditions.  Maintain all equipment installed under the contract until close out documentation is received, the project is completed and the building has been documented as beneficially occupied.

## 3.9   OPERATION AND MAINTENANCE

### 3.9.1   Operation and Maintenance Manuals

Submit six manuals at least 2 weeks prior to field training.  Submit data complying with the requirements specified in Section 01 78 23 OPERATING INSTRUCTIONS AND TRAINING.

### 3.9.2   Operation And Maintenance Training

Conduct a training course for the members of the operating staff as designated by USCG personnel.   Make the training period consist of a total of 8 hours of normal working time and start it after all work specified herein is functionally completed and the Performance Tests have been approved.  Conduct field instruction that covers all of the items contained in the Operation and Maintenance Manuals as well as demonstrations of routine maintenance operations.  Submit the proposed On-site Training schedule concurrently with the Operation and Maintenance Manuals and at least 14 days prior to conducting the training course.

-- End of Section --

SECTION 23 03 00

BASIC MECHANICAL MATERIALS AND METHODS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

ASTM INTERNATIONAL (ASTM)

ASTM B117	(2016) Standard Practice for Operating Salt Spray (Fog) Apparatus

## 1.2   RELATED REQUIREMENTS

This section applies to all sections of Divisions: 23, HEATING, VENTILATING, AND AIR CONDITIONING of this project specification.

## 1.3   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-07 Certificates

Material and Equipment Qualifications

Factory Painting Systems Certification

## 1.4   QUALITY ASSURANCE

### 1.4.1   Material and Equipment Qualifications

Provide materials and equipment that are standard products of manufacturers regularly engaged in the manufacture of such products, which are of a similar material, design and workmanship.  Standard products shall have been in satisfactory commercial or industrial use for 2 years prior to bid opening.  The 2-year use shall include applications of equipment and materials under similar circumstances and of similar size.  The product shall have been for sale on the commercial market through advertisements, manufacturers' catalogs, or brochures during the 2 year period.

### 1.4.2   Alternative Qualifications

Products having less than a two-year field service record will be acceptable if a certified record of satisfactory field operation for not less than 6000 hours, exclusive of the manufacturer's factory or laboratory tests, can be shown.

### 1.4.3   Service Support

The equipment items shall be supported by service organizations.  Submit a certified list of qualified permanent service organizations for support of the equipment which includes their addresses and qualifications.  These service organizations shall be reasonably convenient to the equipment installation and able to render satisfactory service to the equipment on a regular and emergency basis during the warranty period of the contract.

### 1.4.4   Manufacturer's Nameplate

Each item of equipment shall have a nameplate bearing the manufacturer's name, address, model number, and serial number securely affixed in a conspicuous place; the nameplate of the distributing agent will not be acceptable.

### 1.4.5   Modification of References

In each of the publications referred to herein, consider the advisory provisions to be mandatory, as though the word, "shall" had been substituted for "should" wherever it appears.  Interpret references in these publications to the "authority having jurisdiction", or words of similar meaning, to mean the Contracting Officer.

#### 1.4.5.1   Definitions

For the International Code Council (ICC) Codes referenced in the contract documents, advisory provisions shall be considered mandatory, the word "should" shall be interpreted as "shall."  Reference to the "code official" shall be interpreted to mean the "Contracting Officer."  For leased facilities, references to the "owner" shall be interpreted to mean the "lessor."  References to the "permit holder" shall be interpreted to mean the "Contractor."

#### 1.4.5.2   Administrative Interpretations

For ICC Codes referenced in the contract documents, the provisions of Chapter 1, "Administrator," do not apply.  References in the ICC Codes to sections of Chapter 1, shall be applied appropriately by the Contracting Officer as authorized by his administrative cognizance and the FAR.

## 1.5   DELIVERY, STORAGE, AND HANDLING

Handle, store, and protect equipment and materials to prevent damage before and during installation in accordance with the manufacturer's recommendations, and as approved by the Contracting Officer's Representative.  Replace damaged or defective items.

## 1.6   ELECTRICAL REQUIREMENTS

Furnish motors, controllers, disconnects and contactors with their respective pieces of equipment.  Motors, controllers, disconnects and contactors shall conform to and have electrical connections provided under Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM.  Furnish internal wiring for components of packaged equipment as an integral part of the equipment. Extended voltage range motors will not be permitted.  Controllers and contactors shall have a maximum of 120 volt control circuits, and shall have auxiliary contacts for use with the controls furnished.  When motors and equipment furnished are larger than sizes indicated, the cost of additional electrical service and related work shall be included under the section that specified that motor or equipment.  Power wiring and conduit for field installed equipment shall be provided under and conform to the requirements of Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM.

## 1.7   INSTRUCTION TO GOVERNMENT PERSONNEL

When specified in other sections, furnish the services of competent instructors to give full instruction to the designated Government personnel in the adjustment, operation, and maintenance, including pertinent safety requirements, of the specified equipment or system.  Instructors shall be thoroughly familiar with all parts of the installation and shall be trained in operating theory as well as practical operation and maintenance work.

Instruction shall be given during the first regular work week after the equipment or system has been accepted and turned over to the Government for regular operation.  The number of man-days (8 hours per day) of instruction furnished shall be as specified in the individual section.  When more than 4 man-days of instruction are specified, use approximately half of the time for classroom instruction.  Use other time for instruction with the equipment or system.

When significant changes or modifications in the equipment or system are made under the terms of the contract, provide additional instruction to acquaint the operating personnel with the changes or modifications.

## 1.8   ACCESSIBILITY

Install all work so that parts requiring periodic inspection, operation, maintenance, and repair are readily accessible.  Install concealed valves, expansion joints, controls, dampers, and equipment requiring access, in locations freely accessible through access doors.

# PART 2   PRODUCTS

Not Used

# PART 3   EXECUTION

## 3.1   PAINTING OF NEW EQUIPMENT

New equipment painting shall be factory applied or shop applied, and shall be as specified herein, and provided under each individual section.

### 3.1.1   Factory Painting Systems Certification

Manufacturer's standard factory painting systems may be provided subject to certification that the factory painting system applied will withstand 125 hours in a salt-spray fog test, except that equipment located outdoors shall withstand 500 hours in a salt-spray fog test.  Salt-spray fog test shall be in accordance with ASTM B117, and for that test the acceptance criteria shall be as follows:  immediately after completion of the test, the paint shall show no signs of blistering, wrinkling, or cracking, and no loss of adhesion; and the specimen shall show no signs of rust creepage beyond 0.125 inch on either side of the scratch mark.

The film thickness of the factory painting system applied on the equipment shall not be less than the film thickness used on the test specimen.  If manufacturer's standard factory painting system is being proposed for use on surfaces subject to temperatures above 120 degrees F, the factory painting system shall be designed for the temperature service.

-- End of Section --

SECTION 23 05 93

TESTING, ADJUSTING, AND BALANCING OF HVAC SYSTEMS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

ASSOCIATED AIR BALANCE COUNCIL (AABC)

AABC MN-1	(2002) National Standards for Total System Balance

NATIONAL ENVIRONMENTAL BALANCING BUREAU (NEBB)

NEBB TABES	(2005) Procedural Standards for Testing, Adjusting and Balancing of Environmental Systems

SHEET METAL AND AIR CONDITIONING CONTRACTORS' NATIONAL ASSOCIATION (SMACNA)

SMACNA HVACTAB	(2002, 3rd Ed) HVAC Systems - Testing, Adjusting and Balancing

## 1.2   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-02 Shop Drawings

TAB Schematic Drawings and Report Forms

Three copies of the TAB Schematic Drawings and Report Forms, no later than 14 days prior to the start of TAB field measurements.

SD-03 Product Data

TAB Related HVAC Submittals

A list of the TAB Related HVAC Submittals, no later than 7 days after the approval of the TAB Specialist.

TAB Procedures

Proposed procedures for TAB, submitted with the TAB Schematic Drawings and Report Forms.

Calibration

List of each instrument to be used during TAB, stating calibration requirements required or recommended by both the TAB Standard and the instrument manufacturer and the actual calibration history of the instrument, submitted with the TAB Procedures.  The calibration history shall include dates calibrated, the qualifications of the calibration laboratory, and the calibration procedures used.

Systems Readiness Check

Proposed date and time to begin the Systems Readiness Check, no later than 7 days prior to the start of the Systems Readiness Check.

TAB Execution

Proposed date and time to begin field measurements, making adjustments, etc., for the TAB Report, submitted with the Systems Readiness Check Report.

SD-06 Test Reports

Design Review Report

A copy of the Design Review Report, no later than 14 days after approval of the TAB Firm and the TAB Specialist.

Systems Readiness Check

A copy of completed checklists for each system, each signed by the TAB Specialist, at least 7 days prior to the start of TAB Execution.  All items in the Systems Readiness Check Report shall be signed by the TAB Specialist and shall bear the seal of the Professional Society or National Association used as the TAB Standard.  See appendix A of this section for functional checklist.

TAB Report

Three copies of the completed TAB Reports, no later than 7 days after the execution of TAB.  All items in the TAB Report shall be signed by the TAB Specialist and shall bear the seal of the Professional Society or National Association used as the TAB Standard.

Site Visit And Design Review

SD-07 Certificates

TAB Firm

Certification of the proposed TAB Firm's qualifications by either AABC, NEBB, or TABB to perform the duties specified herein and in other related Sections, no later than 21 days after the Notice to Proceed.  The documentation shall include the date that the Certification was initially granted and the date that the current Certification expires.  Any lapses in Certification of the proposed TAB Firm or disciplinary action taken by AABC, NEBB or TABB against the proposed TAB Firm shall be described in detail.

TAB Specialist

Certification of the proposed TAB Specialist's qualifications by either AABC, NEBB, or TABB to perform the duties specified herein and in other related Sections, no later than 21 days after the Notice to Proceed.  The documentation shall include the date that the Certification was initially granted and the date that the current Certification expires.  Any lapses in Certification of the proposed TAB Specialist or disciplinary action taken by AABC, NEBB, or TABB against the proposed TAB Specialist shall be described in detail.

## 1.3   SIMILAR TERMS

In some instances, terminology differs between the Contract and the TAB Standard primarily because the intent of this Section is to use the industry standards specified, along with additional requirements listed herein to produce optimal results.  The following table of similar terms is provided for clarification only.  Contract requirements take precedent over the corresponding AABC, NEBB, or TABB requirements where differences exist.

SIMILAR TERMS

Contract Term      AABC Term                NEBB Term              TABB Term

TAB Standard     National Standards for   Procedural Standards     SMACNA's

Testing and Balancing   for Testing, Adjusting,    Procedures

Heating, Ventilating,     and Balancing of

and Air Conditioning     Environmental Systems.

Systems

TAB Specialist   TAB Engineer             TAB Supervisor           TAB

Supervisor

Systems          Construction Phase       Field Readiness          Field

Readiness        Inspection               Check & Preliminary      Readiness

Check                                               Field Procedures.           Check &

Prelim.

Field

Procedures

## 1.4   GENERAL REQUIREMENTS

Provide complete system testing and balancing as specified herein for the following:  UPH hot water hydronic system, PTHP's, ductless split systems, Kitchen Hood, Kitchen Exhaust Fans, Make-Up Air Unit and Hot Water Coils.

### 1.4.1   Site Visit and Design Review

As soon as practical, but no later 30 than days after award, visit the job site to verify that the correct type and location of balancing devices are in place, or will be provided as part of the work of the project.  Document results of visit in writing, and submit with Design Review Report.

### 1.4.2   Place systems in satisfactory Operating condition

1.  Adjusting and balancing shall be accomplished as soon as systems are complete and before government takes possession.

2.  Prior to balancing, adjust balancing devices to full flow; fill, vent and clean hydronic systems, replace temporary filters and strainers.

3.  Perform initial adjustment of and balancing to quantities indicated, to satisfy job conditions, and to the satisfaction of the COR.

4.  Adjusting and balancing shall be accomplished under appropriate outdoor temperature conditions.

5.  Change pulleys as required to meet system performance requirements.

6.  Perform necessary mechanical adjustments in conjunction with balancing procedure.

7.  Replace balancing cocks and flow balancers in new and existing systems that cannot be manipulated to satisfy balancing requirements.

8.  Replace dampers in new and existing systems that cannot be manipulated to satisfy balancing requirements.

## 1.5   AUTOMATIC TEMPERATURE CONTROL (ATC) SYSTEM SUPPORT

### 1.5.1   Definitions

The terms "Automatic Temperature Controls System (ATC) and "Central Energy Management & Control System (EMCS)" are synonymous.

### 1.5.2   ATC Sub-Contractor Support

This contractor shall engage the services of a qualified ATC system installer to support the TAB effort.  If an ATC Contractor has been engaged for the project, that contractor shall be engaged.  Otherwise, a firm that is conversant with the operation and control of the existing installed or provided HVAC equipment shall be engaged.  This firm is identified herein as the "ATC Sub-contractor."

The ATC Sub-contractor shall manipulate the HVAC systems as required so that TAB of the systems as specified can be accomplished.

## 1.6   TAB STANDARD

TAB shall be performed in accordance with the requirements of the standard under which the TAB Firm's qualifications are approved, i.e., AABC MN-1, NEBB TABES, or SMACNA HVACTAB unless otherwise specified herein.

All recommendations and suggested practices contained in the TAB Standard shall be considered mandatory.

The provisions of the TAB Standard, including checklists and report forms, shall, as nearly as practical, be used to satisfy the Contract requirements.

The TAB Standard shall be used for all aspects of TAB, including qualifications for the TAB Firm and Specialist and calibration of TAB instruments.  Where the instrument manufacturer calibration recommendations are more stringent than those listed in the TAB Standard, the manufacturer's recommendations shall be adhered to.

All quality assurance provisions of the TAB Standard such as performance guarantees shall be part of this contract.

For systems or system components not covered in the TAB Standard, TAB procedures shall be developed by the TAB Specialist.

Where new procedures or requirements applicable to the Contract requirements have been published or adopted by the body responsible for the TAB Standard used (i.e., AABC, NEBB, or TABB) the requirements and recommendations contained in these procedures and requirements shall be considered mandatory.

## 1.7   QUALIFICATIONS

### 1.7.1   TAB Firm

The TAB Firm shall be either a member of AABC or certified by the NEBB or the TABB and certified in all categories and functions where measurements or performance are specified on the plans and specifications, including TAB of environmental systems.  The certification shall be maintained for the performance period of the contract.  If, for any reason, the firm loses subject certification during this period, the Contractor shall immediately notify the Contracting Officer and submit another TAB Firm for approval.

Any firm that has been the subject of disciplinary action by either the AABC, the NEBB, or the TABB within the five years preceding Contract Award shall not be eligible to perform any duties related to the HVAC systems, including TAB.

All work specified in this Section and in other related Sections to be performed by the TAB Firm shall be considered invalid if the TAB Firm loses its certification prior to Contract completion and must be performed by an approved successor.

These TAB services are to assist the Prime Contractor in performing the quality oversight for which it is responsible.  The TAB Firm shall be a subcontractor of the Prime Contractor, shall be financially and corporately independent of the mechanical subcontractor, and shall report to and be paid by the Prime Contractor.

### 1.7.2   TAB Specialist

The TAB Specialist shall be an employee of the TAB Firm, either a member of AABC, an experienced technician of the Firm certified by the NEBB, or a Supervisor certified by the TABB.

The certification shall be maintained for the entire duration of duties specified herein.  If, for any reason, the Specialist loses subject certification during this period, the Contractor shall immediately notify USCG personnel and submit another TAB Specialist for approval.

Any individual that has been the subject of disciplinary action by either the AABC, the NEBB, or the TABB within the five years preceding Contract Award shall not be eligible to perform any duties related to the HVAC systems, including TAB.

All work specified in this Section and in other related Sections performed by the TAB Specialist shall be considered invalid if the TAB Specialist loses his/her certification prior to Contract completion and must be performed by the approved successor.

## 1.8   TAB SPECIALIST RESPONSIBILITIES

All TAB work specified herein and in related sections shall be performed by or under the direct supervision of the TAB Specialist.  The TAB specialist is required to be onsite whenever TAB efforts are conducted.

# PART 2   PRODUCTS

## 2.1   GENERAL REQUIREMENTS

Provide tools, ladders, recording meters, gauges, thermometers, velometers, anemometers, Pitot tubes, inclined gauge manometers, magnehelic gauges, amprobes, voltmeters, psycrometers, tachometers and other instruments as required to perform the TAB of systems specified.  Instruments shall be calibrated by an independent laboratory, with a calibration expiration date after the performance of the TAB efforts.

# PART 3   EXECUTION

## 3.1   DESIGN REVIEW

The TAB Specialist shall visit the site as described in paragraph "GENERAL REQUIREMENTS", review the Contract Plans and Specifications and advise the Contracting Officer of any deficiencies that would prevent the effective and accurate TAB of the system.

The TAB Specialist shall provide a Design Review Report individually listing each deficiency and the corresponding proposed corrective action necessary for proper system operation.

The Design Review Report shall be provided within 30 days of project award, and prior to the start of any mechanical work on-site, unless other arrangements are made with the Contracting Officer.

## 3.2   TAB RELATED HVAC SUBMITTALS

The TAB Specialist shall prepare a list of the submittals from the Contract Submittal Register that relate to the successful accomplishment of all HVAC TAB.

The submittals identified on this list shall be accompanied by a letter of approval signed and dated by the TAB Specialist when submitted to the Contracting Officer.

The TAB Specialist shall also ensure that the location and arrangement of ports, terminals, connections, and other similar features necessary to perform TAB are identified on the submittals, and installed to facilitate TAB efforts.

## 3.3   TAB SCHEMATIC DRAWINGS AND REPORT FORMS

A schematic drawing showing each system component, correlated to the contract drawings (if contract drawings will not clearly suffice for this purpose) including balancing devices, shall be provided for each system.

Each drawing shall be accompanied by a copy of all report forms required by the TAB Standard used for that system.

Where applicable, the acceptable range of operation or appropriate setting for each component shall be included on the forms or as an attachment to the forms.

The schematic drawings shall identify all testing points and cross reference these points to the report forms and procedures, AND the project contract drawings.

## 3.4   DUCTWORK LEAK TESTING

The TAB Specialist shall witness the Ductwork Leak Testing specified in Section 23 00 00 AIR SUPPLY, DISTRIBUTION, VENTILATION, AND EXHAUST SYSTEM and approve the results as specified in Paragraph TAB RELATED HVAC SUBMITTALS.

## 3.5   TESTING, ADJUSTING, AND BALANCING

### 3.5.1   TAB Procedures

Step by step procedures for each measurement required during TAB Execution shall be provided.  The procedures shall be presented in booklet form with a separate section for each system.

The procedures shall include measures to demonstrate that each system performs as specified in all operating modes, interactions with other components (e.g., exhaust fans, kitchen hoods, relief vents) and systems, and with all seasonal operating differences, diversity, simulated loads, and pressure relationships required.

### 3.5.2   Systems Readiness Check

The TAB Specialist shall inspect each system to ensure that it is complete, including installation and operation of controls, and that all aspects of the facility that have any bearing on the HVAC systems, including installation of ceilings, walls, windows, doors, and partitions, are complete to the extent that TAB results will not be affected by any detail or touch-up work remaining.

The TAB Specialist shall also verify that all items such as ductwork and piping ports, terminals, connections, and any other items necessary to perform TAB are complete during the Systems Readiness Check.

### 3.5.3   Preparation of TAB Report

Preparation of the TAB Report shall begin only when the Systems Readiness Report has been approved.

The Report shall be presented in booklet form with a separate section for each system, and contain the following:

1.  Title sheet with Project name, Prime Contractor, mechanical Sub-contractor, TAB Firm, TAB Specialist name, address, telephone number (office and cell phone), web-site, and e-mail address.

2.  Individual test sheets for each air distribution system, exhaust fans, duct traverses, air coils, radiation, and convectors.

3.  Manufacturer's fan curves for equipment installed (normally available through the submittal approval process) with design and actual operating conditions indicated.

4.  One complete set of reproducible record contract drawings marked with terminal unit numbers, register, grille and diffuser numbers that correlate with associated data sheet in TAB report.

5.  Provide commentary of installed system with respect to deviations from Contract Documents not indicating system performance and craftsmanship of the installation.

6.  If specified performance cannot be achieved, notify COR immediately for direction.  Include comment(s) regarding possible causes for inability to achieve design performance.

The Report shall include a copy of the appropriate approved Schematic Drawings and TAB Related Submittals, including pump curves and fan curves as appropriate, along with the completed report forms for each system.

The operating points measured during successful TAB Execution and the theoretical operating points listed in the approved submittals shall be marked on the performance curves and tables.

Where possible, adjustments shall be made using an "industry standard" technique which would result in the greatest energy savings, such as adjusting the speed of a fan instead of throttling the flow.

Any deficiencies outside of the realm of normal adjustments and balancing during TAB Execution shall be noted along with a description of corrective action performed to bring the measurement into the specified range.

If, for any reason, the TAB Specialist determines during TAB Execution that any Contract requirement cannot be met, the TAB Specialist shall immediately provide a written description of the deficiency and the corresponding proposed corrective action necessary for proper system operation to the Contracting Officer.

### 3.5.4   Marking of Setting

The setting of all HVAC adjustment devices including valves, splitters, and dampers shall be permanently marked by the TAB Specialist so that adjustment can be restored if disturbed at any time.

### 3.5.5   Identification of Test Ports

The TAB Specialist shall permanently and legibly identify the location points of duct test ports.  If the ductwork has exterior insulation, the identification shall be made on the exterior side of the insulation.  All penetrations through ductwork and ductwork insulation shall be sealed to prevent air leakage or to maintain integrity of vapor barrier.

## 3.6   TAB PROCEDURES - MINIMUM REQUIREMENTS

The following paragraphs establish minimum Adjusting and Balancing procedures and requirements, and shall be modified as required to demonstrate that installed systems perform as specified.

### 3.6.1   Air Systems - General

1.  Test and adjust fan rpm to design requirements.

2.  Test and record motor no load and full load amperes, and determine operating brake horsepower.

3.  Test and record system static pressures, suction and discharge at AHU inlet and outlet, and upstream and downstream of each coil and filter section.  Correlate pressure readings on a schematic interior elevation/section through the air handling unit (cut in the direction of airflow).

4.  Test and adjust zones and system for design supply, return and exhaust air cfm.

5.  Test and adjust system for design outside air cfm.

6.  Test and record ambient air temperature at time of test.

7.  Test and record entering and leaving air temperatures at coils, both heating and cooling, wet and dry bulb.

8.  Test and adjust zones to proper design supply, return and exhaust cfm.

9.  Adjust terminal units to design cfm.

10.  Test and adjust each diffuser, grille and register to within -5% to +10% of design requirement.

11.  A record of the final setting shall be made on each damper, and at each piece of equipment by an appropriate mark or by description on the TAB report schedule.

### 3.6.2   Systems to be Balanced

Systems or equipment to be TAB'ed include the following:

DCU-1 (HEAT RECOVERY SYSTEM, MAIN BLDG.)

DCU-2 (HEAT RECOVERY SYSTEM, MAIN BLDG.)

DCU-3 (HEAT RECOVERY SYSTEM, MAIN BLDG.)

DCU-3 (DUCTLESS MULTI-ZONE SYSTEM, SHOP BLDG.)

-- End of Section --

SECTION 23 07 00

THERMAL INSULATION FOR MECHANICAL SYSTEMS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.  At the discretion of the Government, the manufacturer of any material supplied will be required to furnish test reports pertaining to any of the tests necessary to assure compliance with the standard or standards referenced in this specification.

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING ENGINEERS (ASHRAE)

ASHRAE 90.1 - IP	(2010; ERTA 2011-2013) Energy Standard for Buildings Except Low-Rise Residential Buildings

ASHRAE 90.1 - SI	(2010; ERTA 2011-2013) Energy Standard for Buildings Except Low-Rise Residential Buildings

ASTM INTERNATIONAL (ASTM)

ASTM A580/A580M	(2015) Standard Specification for Stainless Steel Wire

ASTM B209	(2014) Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

ASTM C1136	(2012) Standard Specification for Flexible, Low Permeance Vapor Retarders for Thermal Insulation

ASTM C1710	(2011) Standard Guide for Installation of Flexible Closed Cell Preformed Insulation in Tube and Sheet Form

ASTM C195	(2007; R 2013) Standard Specification for Mineral Fiber Thermal Insulating Cement

ASTM C450	(2008) Standard Practice for Fabrication of Thermal Insulating Fitting Covers for NPS Piping, and Vessel Lagging

ASTM C534/C534M	(2014) Standard Specification for Preformed Flexible Elastomeric Cellular Thermal Insulation in Sheet and Tubular Form

ASTM C647	(2008; R 2013) Properties and Tests of Mastics and Coating Finishes for Thermal Insulation

ASTM C795	(2008; R 2013) Standard Specification for Thermal Insulation for Use in Contact with Austenitic Stainless Steel

ASTM C916	(2014) Standard Specification for Adhesives for Duct Thermal Insulation

ASTM C920	(2014a) Standard Specification for Elastomeric Joint Sealants

ASTM C921	(2010) Standard Practice for Determining the Properties of Jacketing Materials for Thermal Insulation

ASTM D2863	(2013) Measuring the Minimum Oxygen Concentration to Support Candle-Like Combustion of Plastics (Oxygen Index)

ASTM D5590	(2000; R 2010; E 2012) Standard Test Method for Determining the Resistance of Paint Films and Related Coatings to Fungal Defacement by Accelerated Four-Week Agar Plate Assay

ASTM E2231	(2014) Specimen Preparation and Mounting of Pipe and Duct Insulation Materials to Assess Surface Burning Characteristics

ASTM E84	(2016) Standard Test Method for Surface Burning Characteristics of Building Materials

ASTM E96/E96M	(2013) Standard Test Methods for Water Vapor Transmission of Materials

FM GLOBAL (FM)

FM APP GUIDE	(updated on-line) Approval Guide http://www.approvalguide.com/

INTERNATIONAL ORGANIZATION FOR STANDARDIZATION (ISO)

ISO 2758	(2014) Paper - Determination of Bursting Strength

MIDWEST INSULATION CONTRACTORS ASSOCIATION (MICA)

MICA Insulation Stds	(1999) National Commercial & Industrial Insulation Standards

U.S. DEPARTMENT OF DEFENSE (DOD)

MIL-A-24179	(1969; Rev A; Am 2 1980; Notice 1 1987) Adhesive, Flexible Unicellular-Plastic Thermal Insulation

MIL-PRF-19565	(1988; Rev C) Coating Compounds, Thermal Insulation, Fire- and Water-Resistant, Vapor-Barrier

UNDERWRITERS LABORATORIES (UL)

UL 723	(2008; Reprint Aug 2013) Test for Surface Burning Characteristics of Building Materials

UL 94	(2013; Reprint Sep 2014) Standard for Tests for Flammability of Plastic Materials for Parts in Devices and Appliances

## 1.2   SYSTEM DESCRIPTION

### 1.2.1   General

Provide field-applied insulation and accessories on mechanical systems as specified herein; factory-applied insulation is specified under the piping, duct or equipment to be insulated.  Field applied insulation materials required for use on Government-furnished items as listed in the SPECIAL CONTRACT REQUIREMENTS shall be furnished and installed by the Contractor.

## 1.3   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

Submit the three SD types, SD-02 Shop Drawings, SD-03 Product Data, and SD-08 Manufacturer's Instructions at the same time for each system.

SD-02 Shop Drawings

Pipe Insulation Systems and Associated Accessories

Duct Insulation Systems and Associated Accessories

Equipment Insulation Systems and Associated Accessories

SD-03 Product Data

Pipe Insulation Systems

Duct Insulation Systems

Equipment Insulation Systems

## 1.4   QUALITY ASSURANCE

### 1.4.1   Installer Qualification

Qualified installers shall have successfully completed three or more similar type jobs within the last 5 years.

## 1.5   DELIVERY, STORAGE, AND HANDLING

Materials shall be delivered in the manufacturer's unopened containers.  Materials delivered and placed in storage shall be provided with protection from weather, humidity, dirt, dust and other contaminants.  The COR may reject insulation material and supplies that become dirty, dusty, wet, or contaminated by some other means.  Packages or standard containers of insulation, jacket material, cements, adhesives, and coatings delivered for use, and samples required for approval shall have manufacturer's stamp or label attached giving the name of the manufacturer and brand, and a description of the material, date codes, and approximate shelf life (if applicable).

# PART 2   PRODUCTS

## 2.1   STANDARD PRODUCTS

Provide materials which are the standard products of manufacturers regularly engaged in the manufacture of such products and that essentially duplicate items that have been in satisfactory use for at least 2 years prior to bid opening.  Submit a complete list of materials, including manufacturer's descriptive technical literature, performance data, catalog cuts, and installation instructions.  The product number, k-value, thickness and furnished accessories including adhesives, sealants and jackets for each mechanical system requiring insulation shall be included.  The product data must be copyrighted, have an identifying or publication number, and shall have been published prior to the issuance date of this solicitation.

### 2.1.1   Insulation System

Provide field-applied insulation for heating, ventilating, and cooling (HVAC) air distribution systems and piping systems that are located within, on, under, and adjacent to buildings; and for plumbing systems.  Insulation shall be CFC and HCFC free.

### 2.1.2   Surface Burning Characteristics

Unless otherwise specified, insulation shall have a maximum flame spread index of 25 and a maximum smoke developed index of 50 when tested in accordance with ASTM E84. Flame spread, and smoke developed indexes, shall be determined by ASTM E84 or UL 723. Insulation shall be tested in the same density and installed thickness as the material to be used in the actual construction. Test specimens shall be prepared and mounted according to ASTM E2231.

## 2.2   MATERIALS

Provide insulation that meets or exceed the requirements of ASHRAE 90.1 - IP.  Insulation exterior shall be cleanable, grease resistant, non-flaking and non-peeling.  Materials shall be compatible and shall not contribute to corrosion, soften, or otherwise attack surfaces to which applied in either wet or dry state.  Materials to be used on stainless steel surfaces shall meet ASTM C795 requirements.  Calcium silicate shall not be used on chilled or cold water systems.  Materials shall be asbestos free.  Provide product recognized under UL 94 (if containing plastic) and listed in FM APP GUIDE.

### 2.2.1   Adhesives

#### 2.2.1.1   Acoustical Lining Insulation Adhesive

Adhesive shall be a nonflammable, fire-resistant adhesive conforming to ASTM C916, Type I.

#### 2.2.1.2   Mineral Fiber Insulation Cement

Cement shall be in accordance with ASTM C195.

#### 2.2.1.3   Contact Adhesive

Adhesives may be any of, but not limited to, the neoprene based, rubber based, or elastomeric type that have a maximum flame spread index of 25 and a maximum smoke developed index of 50 when tested in accordance with ASTM E84.  The adhesive shall not adversely affect, initially or in service, the insulation to which it is applied, nor shall it cause any corrosive effect on metal to which it is applied.  Any solvent dispersing medium or volatile component of the adhesive shall have no objectionable odor and shall not contain any benzene or carbon tetrachloride.  The dried adhesive shall not emit nauseous, irritating, or toxic volatile matters or aerosols when the adhesive is heated to any temperature up to 212 degrees F.  The dried adhesive shall be nonflammable and fire resistant.  Flexible Elastomeric Adhesive:  Comply with MIL-A-24179, Type II, Class I.  Provide product listed in FM APP GUIDE.

### 2.2.2   Caulking

ASTM C920, Type S, Grade NS, Class 25, Use A.

### 2.2.3   Corner Angles

Nominal 0.016 inch aluminum 1 by 1 inch with factory applied kraft backing.  Aluminum shall be ASTM B209, Alloy 3003, 3105, or 5005.

### 2.2.4   Fittings

Fabricated Fittings are the prefabricated fittings for flexible elastomeric pipe insulation systems in accordance with ASTM C1710.  Together with the flexible elastomeric tubes, they provide complete system integrity for retarding heat gain and controlling condensation drip from chilled-water and refrigeration systems. Flexible elastomeric, fabricated fittings provide thermal protection (0.25 k) and condensation resistance (0.05 Water Vapor Transmission factor).  For satisfactory performance, properly installed protective vapor retarder/barriers and vapor stops shall be used on high relative humidity and below ambient temperature applications to reduce movement of moisture through or around the insulation to the colder interior surface.

### 2.2.5   Finishing Cement

ASTM C450: Mineral fiber hydraulic-setting thermal insulating and finishing cement.  All cements that may come in contact with Austenitic stainless steel must comply with ASTM C795.

### 2.2.6   Fibrous Glass Cloth and Glass Tape

Fibrous glass cloth, with 20X20 maximum mesh size, and glass tape shall have maximum flame spread index of 25 and a maximum smoke developed index of 50 when tested in accordance with ASTM E84.  Tape shall be 4 inch wide rolls.  Class 3 tape shall be 4.5 ounces/square yard.  Elastomeric Foam Tape: Black vapor-retarder foam tape with acrylic adhesive containing an anti-microbial additive.

### 2.2.7   Jackets

#### 2.2.7.1   Vapor Barrier/Weatherproofing Jacket

Vapor barrier/weatherproofing jacket shall be laminated self-adhesive, greater than 3 plies standard grade, silver, white, black and embossed or greater than 8 ply (minimum 2.9 mils adhesive); with 0.0000 permeability when tested in accordance with ASTM E96/E96M, using the water transmission rate test method; heavy duty, white or natural; and UV resistant.  Flexible Elastomeric exterior foam with factory applied, UV Jacket made with a cold weather acrylic adhesive.  Construction of laminate designed to provide UV resistance, high puncture, tear resistance and excellent Water Vapor Transmission (WVT) rate.

#### 2.2.7.2   Vapor Barrier/Vapor Retarder

Apply the following criteria to determine which system is required.

a.  On ducts, piping and equipment operating below 70 degrees F or located outside shall be equipped with a vapor barrier.

b.  Ducts, pipes and equipment that are located inside and that always operate above 70 degrees F shall be installed with a vapor retarder where required as stated in paragraph VAPOR RETARDER REQUIRED.

### 2.2.8   Vapor Retarder Required

ASTM C921, Type I, minimum puncture resistance 50 Beach units on all surfaces except concealed ductwork, where a minimum puncture resistance of 25 Beach units is acceptable.  Minimum tensile strength, 35 pounds/inch width.  ASTM C921, Type II, minimum puncture resistance 25 Beach units, tensile strength minimum 20 pounds/inch width.  Jackets used on insulation exposed in finished areas shall have white finish suitable for painting without sizing.  Based on the application, insulation materials that require manufacturer or fabricator applied pipe insulation jackets are cellular glass, when all joints are sealed with a vapor barrier mastic, and mineral fiber.  All non-metallic jackets shall have a maximum flame spread index of 25 and a maximum smoke developed index of 50 when tested in accordance with ASTM E84.  Flexible elastomerics require (in addition to vapor barrier skin) vapor retarder jacketing for high relative humidity and below ambient temperature applications.

#### 2.2.8.1   White Vapor Retarder All Service Jacket (ASJ)

ASJ is for use on hot/cold pipes, ducts, or equipment indoors or outdoors if covered by a suitable protective jacket.  The product shall meet all physical property and performance requirements of ASTM C1136, Type I, except the burst strength shall be a minimum of 85 psi.  ASTM D2863 Limited Oxygen Index (LOI) shall be a minimum of 31.

In addition, neither the outer exposed surface nor the inner-most surface contacting the insulation shall be paper or other moisture-sensitive material.  The outer exposed surface shall be white and have an emittance of not less than 0.80.  The outer exposed surface shall be paintable.

#### 2.2.8.2   Vapor Retarder/Vapor Barrier Mastic Coatings

##### 2.2.8.2.1   Vapor Barrier

The vapor barrier shall be self adhesive (minimum 2 mils adhesive,  3 mils embossed) greater than 3 plies standard grade, silver, white, black and embossed white jacket for use on hot/cold pipes.  Permeability shall be less than 0.02 when tested in accordance with ASTM E96/E96M.  Products shall meet UL 723 or ASTM E84 flame and smoke requirements and shall be UV resistant.

##### 2.2.8.2.2   Vapor Retarder

The vapor retarder coating shall be fire and water resistant and appropriately selected for either outdoor or indoor service.  Color shall be white.  The water vapor permeance of the compound shall be 0.013 perms or less at 43 mils dry film thickness as determined according to procedure B of ASTM E96/E96M utilizing apparatus described in ASTM E96/E96M.  The coating shall be nonflammable, fire resistant type.  To resist mold/mildew, coating shall meet ASTM D5590 with 0 growth rating.  Coating shall meet MIL-PRF-19565 Type II (if selected for indoor service) and be Qualified Products Database listed.  All other application and service properties shall be in accordance with ASTM C647.

#### 2.2.8.3   Vapor Barrier/Weather Barrier

The vapor barrier shall be greater than 3 ply self adhesive laminate -white vapor barrier jacket- superior performance (less than 0.0000 permeability when tested in accordance with ASTM E96/E96M).  Vapor barrier shall meet UL 723 or ASTM E84 25 flame and 50 smoke requirements; and UV resistant.  Minimum burst strength 185 psi in accordance with ISO 2758.  Tensile strength 68 lb/inch width (PSTC-1000).  Tape shall be as specified for laminated film vapor barrier above.

### 2.2.9   Wire

Soft annealed ASTM A580/A580M Type 302, 304 or 316 stainless steel, 16 or 18 gauge.

### 2.2.10   Insulation Bands

Insulation bands shall be 1/2 inch wide; 26 gauge stainless steel.

### 2.2.11   Sealants

Sealants shall be chosen from the butyl polymer type, the styrene-butadiene rubber type, or the butyl type of sealants.  Sealants shall have a maximum permeance of 0.02 perms based on Procedure B for ASTM E96/E96M, and a maximum flame spread index of 25 and a maximum smoke developed index of 50 when tested in accordance with ASTM E84.

## 2.3   PIPE INSULATION SYSTEMS

Insulation materials shall conform to Table 1.  Insulation thickness shall meet or exceed the requirements of ASHRAE 90.1 - IP.  Insulation thickness shall be 1 inch.  Pipe insulation materials shall be limited to those listed herein and shall meet the following requirements:

## 2.4   DUCT INSULATION SYSTEMS

### 2.4.1   Exposed Supply Ductwork

Provide factory-applied ASTM C534/C534M Grade 1, Type II, flexible elastomeric closed cell insulation according to manufacturer's recommendations for insulation with insulation manufacturer's standard reinforced fire-retardant vapor barrier, with identification of installed thermal resistance (R) value and out-of-package R value.

### 2.4.2   Concealed Ductwork

Calculate minimum thickness in accordance with ASHRAE 90.1 - IP

### 2.4.3   Exterior Ductwork

Provide double-wall duct work with minimum R-3.5 insulation for exterior installation.  Fabricate inner layer with 22 gauge galvanized steel.  Outer layer shall be fabricated of 22 gauge stainless steel.

## 2.5   EQUIPMENT INSULATION SYSTEMS

Provide manufacturer recommended insulation for new equipment.

# PART 3   EXECUTION

## 3.1   PIPE INSULATION SYSTEMS INSTALLATION

Install pipe insulation systems in accordance with the approved MICA Insulation Stds plates as supplemented by the manufacturers published installation instructions.

### 3.1.1   Pipe Insulation

#### 3.1.1.1   General

Pipe insulation shall be installed on aboveground hot and cold pipeline systems as specified below to form a continuous thermal retarder/barrier, including straight runs, fittings and appurtenances unless specified otherwise.  Installation shall be with full length units of insulation and using a single cut piece to complete a run.  Cut pieces or scraps abutting each other shall not be used.  Pipe insulation shall be omitted on the following:

a.  Pipe used solely for fire protection.

b.  Chromium plated pipe to plumbing fixtures.  However, fixtures for use by the physically handicapped shall have the hot water supply and drain, including the trap, insulated where exposed.

c.  Sanitary drain lines.

d.  Air chambers.

e.  Adjacent insulation.

f.  ASME stamps.

g.  Access plates of fan housings.

h.  Cleanouts or handholes.

#### 3.1.1.2   Pipes Passing Through Walls, Roofs, and Floors

Pipe insulation shall be continuous through the sleeve.

An aluminum jacket or vapor barrier/weatherproofing Jacket or Vapor Barrier/Weatherproofing - self adhesive jacket (minimum 2 mils adhesive,  3 mils embossed) less than 0.0000 permeability, greater than 3 ply standard grade, silver, white, black and embossed with factory applied moisture retarder shall be provided over the insulation wherever penetrations require sealing.

##### 3.1.1.2.1   Penetrate Interior Walls

The aluminum jacket or vapor barrier/weatherproofing - self adhesive jacket (minimum 2 mils adhesive,  3 mils embossed) less than 0.0000 permeability, greater than 3 plies standard grade, silver, white, black and embossed shall extend 2 inches beyond either side of the wall and shall be secured on each end with a band.

##### 3.1.1.2.2   Penetrating Floors

Extend the aluminum jacket from a point below the backup material to a point 10 inches above the floor with one band at the floor and one not more than 1 inch from the end of the aluminum jacket.

##### 3.1.1.2.3   Penetrating Exterior Walls

Continue the aluminum jacket required for pipe exposed to weather through the sleeve to a point 2 inches beyond the interior surface of the wall.

#### 3.1.1.3   Flexible Elastomeric Cellular Pipe Insulation

Flexible elastomeric cellular pipe insulation shall be tubular form for pipe sizes 6 inches and less.  Grade 1, Type II sheet insulation used on pipes larger than 6 inches shall not be stretched around the pipe.  On pipes larger than 12 inches, the insulation shall be adhered directly to the pipe on the lower 1/3 of the pipe.  Seams shall be staggered when applying multiple layers of insulation.  Sweat fittings shall be insulated with miter-cut pieces the same size as on adjacent piping.  Screwed fittings shall be insulated with sleeved fitting covers fabricated from miter-cut pieces and shall be overlapped and sealed to the adjacent pipe insulation.  Type II requires an additional exterior vapor retarder/barrier covering for high relative humidity and below ambient temperature applications.

#### 3.1.1.4   Exposed Piping and Piping in Exposed Areas

All exposed hydronic piping shall be covered with PVC (uv-resistant) insulated fitting covers and jacketing.  PVC fitting covers and jacketing shall be by one manufacturer and provide a protective covering for the systems.

In high abuse areas such as janitor closets and traffic areas in equipment rooms, kitchens, and mechanical rooms, aluminum jackets shall be utilized.  Pipe insulation to the 6 foot level shall be protected.

### 3.1.2   Piping Exposed to Weather

Piping exposed to weather shall have double thickness insulation with aluminum jacket.

#### 3.1.2.1   Aluminum Jacket

The jacket for hot piping may be factory applied.  The jacket shall overlap not less than 2 inches at longitudinal and circumferential joints and shall be secured with bands at not more than 12 inch centers.  Longitudinal joints shall be overlapped down to shed water and located at 4 or 8 o'clock positions.  Joints on piping 60 degrees F and below shall be sealed with metal jacketing/flashing sealant while overlapping to prevent moisture penetration.  Where jacketing on piping 60 degrees F and below abuts an un-insulated surface, joints shall be caulked to prevent moisture penetration.  Joints on piping above 60 degrees F shall be sealed with a moisture retarder.

#### 3.1.2.2   Insulation for Fittings

Flanges, unions, valves, fittings, and accessories shall be insulated and finished as specified for the applicable service.  Two coats of breather emulsion type weatherproof mastic (impermeable to water, permeable to air) recommended by the insulation manufacturer shall be applied with glass tape embedded between coats.  Tape overlaps shall be not less than 1 inch and the adjoining aluminum jacket not less than 2 inches.  Factory preformed aluminum jackets may be used in lieu of the above.  Molded PVC fitting covers shall be provided when PVC jackets are used for straight runs of pipe.  PVC fitting covers shall have adhesive welded joints and shall be weatherproof laminated self-adhesive (minimum 2 mils adhesive,  3 mils embossed) vapor barrier/weatherproofing jacket - less than 0.0000 permeability, (greater than 3 ply, standard grade, silver, white, black and embossed, and UV resistant.

## 3.2   EQUIPMENT INSULATION SYSTEMS INSTALLATION

Install equipment insulation systems in accordance with the approved MICA Insulation Stds plates as supplemented by the manufacturers published installation instructions.

### 3.2.1   General

Removable insulation sections shall be provided to cover parts of equipment that must be opened periodically for maintenance including vessel covers, fasteners, flanges and accessories.  Equipment insulation shall be omitted on the following:

a.  Hand-holes.

b.  Cleanouts.

c.  ASME stamps.

d.  Manufacturer's nameplates.

e.  Duct Test/Balance Test Holes.

### 3.2.2   Equipment Exposed to Weather

#### 3.2.2.1   Installation

Equipment exposed to weather shall be insulated and finished in accordance with the requirements for ducts exposed to weather in paragraph 3.3 DUCT INSULATION INSTALLATION.

#### 3.2.2.2   Optional Panels

At the option of the Contractor, prefabricated metal insulation panels may be used in lieu of the insulation and finish previously specified.  Thermal performance shall be equal to or better than that specified for field applied insulation.  Panels shall be the standard catalog product of a manufacturer of metal insulation panels.  Fastenings, flashing, and support system shall conform to published recommendations of the manufacturer for weatherproof installation and shall prevent moisture from entering the insulation.  Panels shall be designed to accommodate thermal expansion and to support a 250 pound walking load without permanent deformation or permanent damage to the insulation.  Exterior metal cover sheet shall be aluminum and exposed fastenings shall be stainless steel or aluminum.

## 3.3   DUCT INSULATION INSTALLATION

Install duct insulation in accordance with the approved MICA Insulation Stds plates as supplemented by the manufacturers published installation instructions.  Duct insulation minimum thickness and insulation level must meet or exceed the requirements of ASHRAE 90.1 - SI.

-- End of Section --

SECTION 23 09 53

SPACE TEMPERATURE CONTROL SYSTEMS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

ASME INTERNATIONAL (ASME)

ASME B31.1	(2014; INT 1-47) Power Piping

ASME B31.5	(2016) Refrigeration Piping and Heat Transfer Components

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

NEMA 250	(2014) Enclosures for Electrical Equipment (1000 Volts Maximum)

NEMA ST 1	(1988; R 1994; R 1997) Specialty Transformers (Except General Purpose Type)

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 70	(2017) National Electrical Code

NFPA 90A	(2015) Standard for the Installation of Air Conditioning and Ventilating Systems

U.S. FEDERAL COMMUNICATIONS COMMISSION (FCC)

FCC Part 15	Radio Frequency Devices (47 CFR 15)

UNDERWRITERS LABORATORIES (UL)

UL 508	(1999; Reprint Oct 2013) Industrial Control Equipment

## 1.2   SYSTEM DESCRIPTION

Provide new space temperature control systems complete and ready for operation for spaces served by new HVAC equipment indicated on the design documents.

## 1.3   SYSTEM REQUIREMENTS

Provide control systems composed of any combination of electric, microprocessor, or analog electronic devices.  Indicated control system devices of a particular type do not intend a requirement for the device unless the requirement is specifically indicated.  Requirements apply to field installed control systems.

Inspect and test existing control systems, components contained in the UPH mechanical room operating the hot water generating system (ie. boiler pumps, aquastats, etc.) and furnish a report to the Contracting Officer identifying all inoperative components or system deficiencies.  The report shall include a cost estimate to correct deficiencies, scheduled need dates for equipment shutdown for repairs and connection to existing controls and systems.  Proceed with repairs only after receipt of Contracting Officer approval.  Diagnose and report any malfunctions of existing control system device that occurs after the work commences.  The Government is responsible for maintenance and repair of Government equipment.  The Contractor shall be held responsible for repair costs due to Contractor negligence or abuse of Government equipment.

## 1.4   PERFORMANCE REQUIREMENTS

Provide control systems to maintain the required heating, ventilating, and cooling (HVAC) conditions by performing the functions and sequences of operations indicated.  Control systems shall be complete, including all equipment and appurtenances, and ready for operation.  Control systems shall be furnished, installed, tested, calibrated, and started up by, or under the supervision of trained technicians certified by the Contractor as qualified and regularly employed in such work.  Control system equipment, valves, panels and dampers shall bear the manufacturer's nameplate.

## 1.5   DESIGN REQUIREMENTS

### 1.5.1   Control System Diagrams

For each system, indicate HVAC process flow and location of devices relative to flow and to the HVAC control panel, the connections of control devices in control loops, references of control device contacts and device operating coils to line numbers of a ladder diagram and sequencing diagrams showing the operation of valves, dampers, and contacts relative to controller output, and HVAC process variables.

### 1.5.2   Ladder Diagram

Indicate connections and interlocks to control system devices and other devices such as starters, and HVAC equipment panels.  Diagram shall be coordinated by line number and device number with each control system diagram.

### 1.5.3   Operating Parameters

Indicate operating parameters for devices shown on the control system diagram such as setpoints, ranges, limits, differentials, outside air temperature schedules, contact operating points, and HVAC equipment operating time schedules.

### 1.5.4   Wiring Diagram

Indicate terminal blocks, wire marker identification, connections to control system devices, external and internal power sources, and connections to external devices, starters, control panels, jumpers, and ground connections.

### 1.5.5   Sequence of Operation

See design drawings for required sequence of operation to be performed by equipment.  Submit sequence of operation for each HVAC control system coordinated with device identifiers on control system diagram and ladder diagram.

## 1.6   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-02 Shop Drawings

Control system diagrams for each HVAC system

Ladder diagram

Operating parameters

Sequence of operation

Wiring diagram

SD-03 Product Data

Actuators

Valves

Thermostats

Indicating devices

Controllers

SD-06 Test Reports

Commissioning procedures

Calibration adjustment and commissioning reports

Site testing procedures identifying each item tested and describing each test

Performance verification test plans and procedures

Notification Of Planned Testing

Test Procedure

Written Report

Test Review Meeting

SD-07 Certificates

Certification of completion

SD-10 Operation and Maintenance Data

Space temperature control system

Submit in accordance with Section 01 78 23 OPERATING INSTRUCTIONS AND TRAINING.

Training

SD-11 Closeout Submittals

Qualified service organization list

## 1.7   QUALITY ASSURANCE

### 1.7.1   Standard Products

a.  Material and equipment shall be standard products of manufacturers regularly engaged in the manufacturing of such products, using similar materials, design and workmanship.  The standard products shall have been in satisfactory commercial or industrial use for 2 years prior to bid opening.  The 2-year use shall include applications of similarly sized equipment and materials used under similar circumstances.

The 2 years’ experience must be satisfactorily completed by a product which has been sold or is offered for sale on the commercial market through advertisements, manufacturers' catalogs, or brochures.  Products having less than a 2-year field service record will be acceptable if a certified record of satisfactory field operation, for not less than 6000 hours exclusive of the manufacturer's factory tests, can be shown.

b.  The equipment items shall be supported by a service organization.

### 1.7.2   Verification of Dimensions

Contractor shall become familiar with details of work, shall verify dimensions in the field, and shall advise Contracting Officer of any discrepancy before performing work.

### 1.7.3   Modification of References

Accomplish work in accordance with ASME B31.1, ASME B31.5, NFPA 70, and NFPA 90A, except as modified herein or indicated otherwise for equipment, materials, installation, examination, inspection, and testing.  Consider the advisory or recommended provisions to be mandatory, as though the word "shall" had be substituted for the words "should" or "could" or "may," wherever they appear.  Interpret reference to "authority having jurisdiction" and "owner" to mean the Contracting Officer.

### 1.7.4   Site Testing Procedures

Indicate test equipment to be used including manufacturers' names and model numbers, date of last calibration, and accuracy of calibration.

### 1.7.5   Commissioning Procedures

Define procedures specific to each control system including instructions on how to set control parameters and setpoints, proportional, integral and derivative mode constants, contact output settings, positioner range adjustments, and calibration checks of transmitters

### 1.7.6   Calibration Adjustment and Commissioning Reports

Submit specific to each HVAC control system, including settings adjustments and results of calibration checks

### 1.7.7   Space Temperature Control System

In addition to the requirements specified in the paragraph entitled "SUBMITTALS", meet the following requirements.  Submit Operation and Maintenance Manuals for items of equipment listed under paragraph entitled "Product Data."  Manual shall contain full hardware support documentation, which shall include but not be limited to the following:

a.  General description and specifications

b.  Installation and initial checkout procedures

c.  Detailed electrical and logical description

d.  Troubleshooting procedures, diagrams, and guidelines

e.  Alignment and calibration procedures for components

f.  Preventive maintenance requirements and a maintenance checklist

g.  Detailed schematics and assembly drawings

h.  Spare parts list data, including required tool kits and suggested method of repairs such as field repair, factory repair, or item replacement

i.  Signal identification and timing diagrams

j.  Complete as-built control drawings, schedules, and sequence of operation

k.  Controller configuration and parameter setting procedures

l.  Step-by-step procedures required for each HVAC control systems startup, operation, shutdown, recovery, and fault diagnosis

m.  Manufacturer supplied operator manuals for equipment

n.  Qualified service organization list

### 1.7.8   Glycol Resistance

All valve surfaces and sealing elements exposed to the hydronic system fluid shall be approved by the manufacturer for use in systems containing a propylene glycol solution concentration up to 40%.

# PART 2   PRODUCTS

## 2.1   COMPONENTS

Provide components factory ordered for this project.  Rebuilt equipment, warehoused equipment, or earlier generation equipment shall not be acceptable.  Electrical, electronic, and electropneumatic devices not located within control panels shall have a NEMA 250 Type 1 enclosure in accordance with NEMA 250 unless otherwise specified.  Actuators and positive positioners, and transmitters shall operate within temperature limit ratings of plus 35 to 150 degrees F.  Panel mounted instruments shall operate within limit ratings of 35 to 120 degrees F and 10 percent to 95 percent relative humidity, noncondensing.  Devices installed outdoors shall operate within limit ratings of minus 35 to 150 degrees F.

## 2.2   ACTUATORS

Provide electric actuators.  Actuators shall function as required within 85 to 110 percent of their power supply rating. Actuators shall fail to their spring return positions on signal or power failure unless indicated as timed, power return actuators.  Actuators shall have visible position indicators.  Actuators shall open or close the devices to which they are applied within 60 seconds after a full scale signal input change.  Pneumatic actuators shall be rated for 25 psig operating pressure except for high pressure cylinder type actuators.

## 2.3   THERMOSTATS

Provide thermostats.

### 2.3.1   Microprocessor-Based Room Thermostats

Microprocessor-based room thermostats shall have built-in keypads for scheduling of day and night temperature settings.  When out of the scheduling mode, thermostats shall have continuous 12-hour time display, with AM and PM indication, continuous display of day of the week, and either continuous display of room temperature with display of temperature setpoint on demand, or continuous display of temperature setpoint with display of room temperature on demand.  In the programmable mode, use the display for setting and interrogating time program ON-OFF setpoints for each day of the week.  The time program shall allow two separate temperature setback intervals per day.  Thermostats shall have a means for temporary and manual override of program schedule, with automatic program restoration on the following day.  Thermostats shall have a replaceable battery to maintain timing and to maintain the schedule in memory for one year in the event of a power outage.  Maximum differential shall be 2 degrees F.  Where used for heat pump applications, thermostat shall have an emergency heat switch.

### 2.3.2   Low-Temperature Protection Thermostats (Freezestats)

Low-temperature protection thermostats shall be manually reset low-temperature safety thermostats, with NO and NC contacts or a two-position pneumatic output signal and a 20 foot element which shall respond to the coldest 18 inch segment.

## 2.4   INDICATING DEVICES

Provide indicating devices.

## 2.5   CONTROLLERS

### 2.5.1   Single-Loop Controllers

#### 2.5.1.1   Controller Features

Controller shall be a microprocessor-based, single-loop device that does not require Contractor-generated software.  Controller shall conform to FCC Part 15.  Controller panel cutout shall be 3.62 by 3.62 inches.  Controller shall have field selectable range for process variables, a remote setpoint analog input and analog output with adjustable high and low end limits, and proportional control manual reset adjustment.   Analog output shall result from PID control.  Analog output shall be configurable as direct acting and reverse acting.  Controller shall have keyboard, display, auto/manual selection for control of analog output, and remote setpoint adjustment/local setpoint adjustment selection.  Controller shall have adjustable high-end and low-end limits, ratio, and bias adjustments on remote setpoint input; operator initiated self-tune/manual-tune selection, anti-reset wind-up feature, and two configurable independent SPDT with adjustable system contact closure outputs.  Controller shall be configurable to power-up in manual with local setpoint control, in automatic with local setpoint control, and in automatic with remote setpoint control.  Contact closures shall be activated by a process variable and by a process variable deviation from setpoint as configured.  The range of hysteresis adjustment shall not be smaller than 1 percent to 5 percent of process variable input span.  Controller shall power the analog output loop to 20 mA where connected to a load of 600 ohms.  Controller shall have 5-year battery backup or shall have nonvolatile memory to store operating parameters.

#### 2.5.1.2   Controller Parameter Input and Display

Control parameters shall be entered and displayed directly, in the correct engineering units, through a series of keystrokes on a front panel display with a 3 1/2-digit, seven-segment display, with decimal point and polarity indication.  Use of the display shall allow manual interrogation of setpoint, mode constants, and values of process variables and outputs.

#### 2.5.1.3   Controller Electrical Requirements

Controller shall be powered by 120 Vac.  Controller shall provide electrical noise isolation, not less than 100 dB at 60 Hz common mode rejection ratio, and not less than 60 dB at 60 Hz normal mode rejection ratio between ac power line and process variable input, remote setpoint input, and output signals.

#### 2.5.1.4   Controller Accuracy

Controller shall have an accuracy of plus or minus 0.30 percent of input span, plus or minus one digit.

#### 2.5.1.5   Controller Self Tuning

Controller self-tuning operation shall apply proportional, integral, and derivative modes of control; mode constants shall be modified as required.   Self tuning shall only operate when selected from the front panel.

#### 2.5.1.6   Controller Manual Tuning

Controller manual tuning operation shall provide proportional, integral, and derivative control modes, or any combination thereof, by means of individual mode constant adjustments.  Adjustments shall be set for the appropriate value if a particular control mode action is desired, or to zero for the particular mode not desired.  The proportional mode constant shall be adjustable from 0 to 200 percent of input signal range; the integral mode constant shall be adjustable from 0 to 20 repetitions per minute; and the derivative mode constant shall be adjustable from 0 to 5 minutes.

### 2.5.2   Analog Electronic Controllers

Controllers shall be solid-state electronic devices which sense the difference between input sensor analog values (resistance or voltage) and setpoint adjustment analog values (resistance or voltage), and shall amplify the difference signal to provide the output signal.  Controllers shall include the following:

a.  Proportional band:  2.5 to 33 percent of input device span.

b.  Authority:  minimum of 33 to 200 percent.

c.  Inputs:  thermistor, resistance, transmitter, or output of other electronic controllers.

d.  Outputs:  within the range of minus 5 to 20 Vdc or a 4 to 20 mA dc current loop.

e.  Remote setpoint adjustment (SPA):  plus or minus 10 percent of input device span.

### 2.5.3   Unitary Control Systems

Unitary control systems shall be energy-efficient, micro-processor-based temperature controllers and associated devices that do not require Contractor-generated software.  Provide control systems with integral or remote sensor as indicated.  Controllers shall operate heating, cooling, and ventilating modes with independent occupied and unoccupied settings and cooling modes.  Provide a one minute minimum time delay between the start and stop operation of heating and cooling stages upon startup and after power failure to prevent short cycling and power surges.  Controller shall have a self-diagnostic program to indicate errors and locking covers to prevent unauthorized program entries.  Provide a convenient means to restore the occupied mode of operation for a minimum 2-hour period without removing covers.  An indexing switch shall allow operation in a continuous unoccupied mode during abnormal periods without changing normal programs.

## 2.6   CONTROL DEVICES AND ACCESSORIES

Provide control devices and accessories.

### 2.6.1   Relays

Relays shall be two-pole, double-throw (DPDT) with a 10-ampere resistive rating at 24 Vac, and shall have an enclosed coil.  Provide with a light indicator which is lit when the coil is energized and is not lit when the coil is not energized.

### 2.6.2   Time-Delay Relays

Time-delay relays shall be DPDT with octal connectors and dust covers.  The adjustable timing range shall be 0 to 3 minutes.

### 2.6.3   Regulated Power Supplies

Power supplies shall provide a 24-Vdc linear supply at not less than 2 amperes, with regulation to 0.05 percent of output voltage.  Power supplies shall have a fused input, and shall be protected from voltage surges and power-line transients.  Power supply output shall be protected against overvoltage and short circuits.  Power supply loading shall not be greater than 1.2 amperes.

### 2.6.4   Transformers

UL 508 and NEMA ST 1 as applicable.  Transformers, other than transformers in bridge circuits, shall have primaries wound for available voltage and secondaries wound for correct control circuit voltage.   Transformers shall be sized so that connected loads equal 80 percent of rated capacity.  Transformers shall be enclosed in rustproof, galvanized steel cabinets with conduit connections.  Disconnect switch shall be provided on the primary side, and a fuse cutout on the secondary side.

## 2.7   CONTROL WIRING

Provide HVAC control wiring.

### 2.7.1   Wiring

a.  Terminal blocks shall be insulated, modular, feed-through, clamp style with recessed captive screw-type clamping mechanisms.  Terminal blocks shall be rail mounted, and shall have end plates, partition plates or enclosed sides for separation.

b.  Control wiring for 24-V circuits shall be 18 AWG minimum and shall be rated for 300-V service.

c.  Wiring for circuits operating at more than 100 V shall be 14 AWG minimum and shall be rated for 600-V service.

d.  Analog signal wiring circuits within control panels shall not be less than 20 AWG and shall be rated for 300-V service.

e.  Instrumentation cable shall be 18 AWG, stranded copper, single or multiple twisted, minimum 2-inch lay of twist, 100 percent shielded pairs, and shall have 300-V insulation.  Each pair shall have a 20-AWG tinned copper drain wire, individual pair, and overall insulation.  Cables shall have an overall aluminum polyester or tinned overall copper cable shield tape, 20-AWG tinned-copper cable drain wire, and overall cable insulation.

f.  Nonconducting wiring ducts in control panels shall have slotted side snap-on covers, fittings for connecting ducts, mounting clips for securing ducts, and wire retaining clips.

# PART 3   EXECUTION

## 3.1   INSTALLATION

Perform installation under the supervision of competent technicians regularly employed in the installation of control systems.  Provide components for a complete and operational control system.  Provide control system complete and ready for operation, as specified and indicated.   Provide dielectric isolation where dissimilar metals are used for connection and support.  Penetrations through and mounting holes in the building exterior shall be watertight.  Control system installation shall provide adequate clearance for control system maintenance by maintaining access spaces between coils, plenums, and as required to calibrate, remove, repair, or replace control system devices.  Control system installation shall not interfere with the clearance requirements for mechanical and electrical system maintenance.  Install devices mounted in or on piping or ductwork, on building surfaces, in mechanical and electrical spaces, or in occupied space ceilings in accordance with manufacturer's recommendations and as indicated on contract documents.  Provide control devices to be installed in piping and ductwork with required gaskets, flanges, thermal compounds, insulation, piping, fittings, and manual valves for shutoff, equalization, purging, and calibration.  Certify that installation of control system is complete and technical requirements of this section have been met.

### 3.1.1   Sensors

Provide sensors in locations to sense the appropriate condition.  Install sensor and transmitter where easily accessible and serviceable without special tools.  Sensors shall be calibrated to the accuracy specified in the contract, and operate correctly when installed.  Do not install sensors designed for one application in the place of another application (e.g., replacing a duct sensor with a room sensor).

#### 3.1.1.1   Room Sensors

Provide on interior walls to sense average room conditions.  Avoid locations which may be covered by furniture.  Do not mount room sensors on exterior walls if other locations are available.  Mount centerline of sensor 5 feet above finished floor.

#### 3.1.1.2   Low-Temperature Protection Thermostats (Freezestats)

Provide thermostat for each 80 square feet of coil-face area to sense the temperature at location indicated.  Install thermostat sensing element in serpentine pattern.  Ensure sensing element provides coverage of the corners and perimeter of the coil-face area.

### 3.1.2   Valves

Provide valve with stems upright where possible but with stems not lower than horizontal.  Provide positioners where indicated and where necessary to prevent overlap of heating and cooling where one controller operates more than one pneumatic device and to maintain the proper dead band between heating and cooling.

### 3.1.3   Wiring

a.  Provide wiring external to control panels, including low-voltage wiring, in metallic raceways.  Install wiring without splices between sensors, transmitters, control devices, and HVAC control panels.  Install instrumentation grounding as necessary to prevent ground loops, noise, and surges adversely affecting operation of the system.  Tag cables, conductors, and wires at both ends, with identifiers indicated on shop drawings.

b.  Other electrical work shall be specified in Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM.  Provide step-down transformers where control equipment operates at lower than line circuit voltages.  Transformers serving individual heating, ventilating, and air-conditioning units shall be fed from fan motor leads, or fed from the nearest distribution panelboard or motor control center, using circuits provided for that purpose.

c.  Ground control panels and cabinets as specified in Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM.  Grounding of the green ac ground wire at the breaker panel alone is not adequate.  Install ground wire from each control panel to adequate building ground.

## 3.2   ADJUSTMENTS

Calibrate instrumentation and controls, and verify specified accuracy using test equipment traceable to National Institute for Science and Technology (NIST) standards.  Adjust controls and equipment to maintain conditions indicated, to perform the functions indicated, and to operate in the sequence specified.

## 3.3   FIELD QUALITY CONTROL

a.  Demonstrate compliance of HVAC control systems.  Furnish personnel, equipment, instrumentation, and supplies necessary to perform calibration and site testing.  Calibrate test equipment in accordance with NIST standards.  Ensure that tests are performed or supervised by competent employees of the control system installer or the control system manufacturer regularly employed in testing and calibration of control systems.

b.  Testing shall include field tests and the performance verification test.  Field tests shall demonstrate proper calibration of instrumentation, input and output devices, and operation of specific equipment.  The performance verification test shall ensure proper execution of sequence of operation and proper tuning of control loops.

c.  The plan for each phase of field acceptance testing shall be approved in writing before beginning that phase of testing.  Furnish written notification of planned testing to Contracting Officer at least 21 days prior to testing.  Include proposed test procedures with notification.  The Contractor will not be allowed to start testing without written Government approval of test procedures.  Test procedures shall consist of detailed instructions for complete testing to prove the performance of heating, ventilating, and air-conditioning system and control system.

d.  Submit original copies of data produced, including results of each test procedure, to the Government at the conclusion of each phase of testing.  Tests are subject to supervision and approval by Contracting Officer.  Do not perform testing during scheduled seasonal off-periods of heating and cooling systems.

### 3.3.1   Test Reporting

After completion or termination of field tests and again after the performance verification test, identify, determine causes, replace, repair, or calibrate equipment which fails to meet the specification; and deliver a written report to the Contracting Officer.  The report shall document test results, explain in detail the nature of each failure, and corrective action taken.  After delivering the performance verification test report, the Contractor shall convene a test review meeting at the job site to present results and recommendations to the Contracting Officer and Contracting Officer's Representative.  As a part of the test review meeting, the Contractor shall demonstrate by performing appropriate portions of field tests or the performance verification test that failures have been corrected.  Based on Contractor's report and test review meeting, the Contracting Officer will determine either the restart point or successful completion of testing.  Do not commence required retesting until after receipt of written notification by the Contracting Officer.  At the conclusion of retesting, repeat the assessment.

### 3.3.2   Contractor's Field Testing

Calibrate field equipment and verify equipment and system operation before system is placed on-line.

#### 3.3.2.1   Wiring Integrity Tests

Test wiring for continuity, ground faults, and open and short circuits.

#### 3.3.2.2   System Inspection

Observe HVAC control system in shutdown condition.  Check dampers and valves for proper normal positions.  Document positions for the performance verification test report.

#### 3.3.2.3   Calibration Accuracy and Operation of Input Test

Verify correct calibration and operation of input instrument.  For each sensor and transmitter, including for temperature, pressure, relative humidity, and dew point inputs, record the reading at the sensor or transmitter location using calibrated test equipment.  Record the output reading provided by that sensor or transmitter.  Document each of the locations and output readings for the performance verification test report.   The test equipment shall have been calibrated within one year of the date of use in the field.  Test equipment calibration shall be traceable to the measurement standard of the National Institute of Standards and Technology.

#### 3.3.2.4   Operation of Output Test

Check the operation of output to verify correct operation.  Operate analog device to minimum range (e.g., 4 mA) and maximum range (e.g., 20 mA), and measure and record actual output values.

#### 3.3.2.5   Actuator Range Adjustment

With the controller, apply a control signal to each actuator and verify that the actuator operates properly from its normal position through to the full range of stroke position.  Record actual spring ranges and normal positions for modulating control valves and dampers.

### 3.3.3   Coordination With HVAC System Balancing

Tune the control system after air and hydronic systems have been balanced, minimum damper positions have been set, and a report has been issued.

### 3.3.4   Field Test Documentation

Before scheduling the performance verification test, provide field test documentation and written certification of completion to Contracting Officer, that the installed system has been calibrated, tested, and is ready to begin the performance verification test.  Do not start the performance verification test prior to receiving written permission from the Contracting Officer's Representative.

### 3.3.5   Performance Verification Test

Conduct the performance verification tests to demonstrate that the control system maintains setpoints and that the control loops are tuned for the correct sequence of operation.  Conduct the performance verification test during one week of continuous HVAC and control systems operation and before final acceptance of work.  Specifically, the performance verification test shall demonstrate that the HVAC system operates properly through the complete sequence of operation (e.g., seasonal, occupied and unoccupied, warm up, etc.), for specified control sequences.  Demonstrate proper control system response for abnormal conditions for which there is a specified system or controls response by simulating these conditions.  Demonstrate that hardware interlocks and safety devices work as designed.  Demonstrate that the control system performs the correct sequence of control.

### 3.3.6   Opposite Season Test

Repeat the performance verification test during an opposite season to the first performance verification test.

## 3.4   TRAINING

Provide a qualified instructor to conduct training courses for designated personnel in maintenance and operation of HVAC and control systems.  Orientate training to the specific system being installed under the contract.  Furnish audiovisual equipment and other training materials and supplies.  A training day is defined as 8 hours of classroom and field instruction, including two 15-minute breaks and excluding lunch time, Monday through Friday, during the daytime shift in effect at the training facility.  For guidance, assume that the attendees have a high school education and are familiar with HVAC systems.  Submit planned training schedule, agenda, and class materials to the Contracting Officer at least 45 days prior to training.  Time and schedule of training shall be coordinated with on-site USCG personnel and Contracting Officer's Representative.

### 3.4.1   System Maintenance Training

Course shall be taught at the project site within one month after completion of endurance test for a period of 1 training day.  Maximum of 5 personnel shall attend the course.  Course shall include but not be limited to the following:

a.  Physical layout for each piece of hardware

b.  Troubleshooting and diagnostics procedures

c.  Repair instructions

d.  Preventive maintenance procedures and schedule

e.  Calibration procedures

## 3.5   QUALIFIED SERVICE ORGANIZATION LIST

The qualified service organization list shall include names and telephone numbers of organizations qualified to service HVAC control systems.

## 3.6   COMMISSIONING

Commissioning of control systems is specified in the pre-field TAB engineering report described in Section 23 05 93 TESTING, ADJUSTING, AND BALANCING FOR HVAC SYSTEMS.

## 3.7   SEQUENCES OF OPERATION

Refer to M-series drawings.

-- End of Section --

SECTION 23 23 00

REFRIGERANT PIPING

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AIR-CONDITIONING, HEATING AND REFRIGERATION INSTITUTE (AHRI)

AHRI 710	(2009) Performance Rating of Liquid-Line Driers

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING ENGINEERS (ASHRAE)

ANSI/ASHRAE 15 & 34	(2013; Addenda A 2014; ERTA 1 2014; Addenda A-T AND SUPP 2015; ERTA 2 2015; INT 1 2015; ERTA 3 2015; ERTA 4 2016; INT 2-3 2016) ANSI/ASHRAE Standard 15-Safety Standard for Refrigeration Systems and ANSI/ASHRAE Standard 34-Designation and Safety Classification of Refrigerants

AMERICAN WELDING SOCIETY (AWS)

AWS A5.8/A5.8M	(2011; Amendment 2012) Specification for Filler Metals for Brazing and Braze Welding

AWS BRH	(2007) Brazing Handbook

ASME INTERNATIONAL (ASME)

ASME B16.22	(2013) Standard for Wrought Copper and Copper Alloy Solder Joint Pressure Fittings

ASME B16.26	(2013) Standard for Cast Copper Alloy Fittings for Flared Copper Tubes

ASME B31.1	(2014; INT 1-47) Power Piping

ASME B31.5	(2016) Refrigeration Piping and Heat Transfer Components

ASME BPVC SEC IX	(2010) BPVC Section IX-Welding and Brazing Qualifications

ASTM INTERNATIONAL (ASTM)

ASTM A 53/A 53M	(2007) Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless

ASTM A 653/A 653M	(2009a) Standard Specification for Steel Sheet, Zinc-Coated (Galvanized) or Zinc-Iron Alloy-Coated (Galvannealed) by the Hot-Dip Process

ASTM B 117	(2009) Standing Practice for Operating Salt Spray (Fog) Apparatus

ASTM B 280	(2008) Standard Specification for Seamless Copper Tube for Air Conditioning and Refrigeration Field Service

ASTM B 32	(2008) Standard Specification for Solder Metal

ASTM B 62	(2009) Standard Specification for Composition Bronze or Ounce Metal Castings

ASTM B 75	(2002) Standard Specification for Seamless Copper Tube

ASTM B 813	(2000; R 2009) Standard Specification for Liquid and Paste Fluxes for Soldering of Copper and Copper Alloy Tube

ASTM D 3308	(2006) PTFE Resin Skived Tape

ASTM D 520	(2000; R 2005) Zinc Dust Pigment

ASTM E 84	(2013a) Standard Test Method for Surface Burning Characteristics of Building Materials

MANUFACTURERS STANDARDIZATION SOCIETY OF THE VALVE AND FITTINGS INDUSTRY (MSS)

MSS SP-58	(2009) Pipe Hangers and Supports - Materials, Design and Manufacture, Selection, Application, and Installation

MSS SP-69	(2003; Notice 2012) Pipe Hangers and Supports - Selection and Application (ANSI Approved American National Standard)

## 1.2   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-03 Product Data

Refrigerant Piping System

Manufacturer's standard catalog data, at least 5 weeks prior to the purchase or installation of a particular component, highlighted to show material, size, options, performance charts and curves, etc. in adequate detail to demonstrate compliance with contract requirements.  Include in the data manufacturer's recommended installation instructions and procedures.  Provide data for the following components as a minimum:

Pipe, Fittings And End Connections (Joints)

Valves

Piping Accessories

Pipe Hangers, Inserts, And Supports

## 1.3   QUALITY ASSURANCE

### 1.3.1   Qualifications

Piping shall be welded in accordance with the qualified procedures using performance qualified welders and welding operators.  Procedures and welders shall be qualified in accordance with ASME BPVC SEC IX.  Welding procedures qualified by others, and welders and welding operators qualified by another employer may be accepted as permitted by ASME B31.1.  Notify the Contracting Officer's Representative 24 hours in advance of tests to be performed at the work site, if practical.  The welder or welding operator shall apply the personally assigned symbol near each weld made, as a permanent record.

### 1.3.2   Contract Drawings

Because of the small scale of the drawings, it is not possible to indicate all offsets, fittings, and accessories that may be required.  Carefully investigate the plumbing, fire protection, electrical, structural and finish conditions that would affect the work to be performed and arrange such work accordingly, furnishing required offsets, fittings, and accessories to meet such conditions.

## 1.4   DELIVERY, STORAGE, AND HANDLING

Protect stored items from the weather, humidity and temperature variations, dirt and dust, or other contaminants.  Proper protection and care of all material both before and during installation is the Contractor's responsibility.  Replace any materials found to be damaged at the Contractor's expense.  During installation, cap piping and similar openings to keep out dirt and other foreign matter.

## 1.5   MAINTENANCE

### 1.5.1   General

Operation and maintenance data shall comply with the requirements of Section 01 78 23 OPERATING INSTRUCTIONS AND TRAINING and as specified herein.

# PART 2   PRODUCTS

## 2.1   STANDARD COMMERCIAL PRODUCTS

a.  Provide materials and equipment which are standard products of a manufacturer regularly engaged in the manufacturing of such products, that are of a similar material, design and workmanship and that have been in satisfactory commercial or industrial use for 2 years prior to bid opening.

b.  The 2 year use shall include applications of equipment and materials under similar circumstances and of similar size.  The 2 years’ experience shall be satisfactorily completed by a product which has been sold or is offered for sale on the commercial market through advertisements, manufacturer's catalogs, or brochures.  Products having less than a 2 year field service record will be acceptable if a certified record of satisfactory field operation, for not less than 6000 hours exclusive of the manufacturer's factory tests, can be shown.

c.  Products shall be supported by a service organization.  System components shall be environmentally suitable for the indicated locations.

## 2.2   REFRIGERANT PIPING SYSTEM

Refrigerant piping, valves, fittings, and accessories shall be in accordance with ANSI/ASHRAE 15 & 34 and ASME B31.5, except as specified herein.  Refrigerant piping, valves, fittings, and accessories shall be compatible with the fluids used and capable of withstanding the pressures and temperatures of the service.  Refrigerant piping, valves, and accessories used for refrigerant service shall be cleaned, dehydrated, and sealed (capped or plugged) prior to shipment from the manufacturer's plant.

## 2.3   PIPE, FITTINGS AND END CONNECTIONS (JOINTS)

### 2.3.1   Copper Tubing

Copper tubing shall conform to ASTM B 280 annealed or hard drawn as required.  Copper tubing shall be soft annealed where bending is required and hard drawn where no bending is required.  Soft annealed copper tubing shall not be used in sizes larger than 1-3/8 inches.  Joints shall be brazed except that joints on lines 7/8 inch and smaller may be flared.  Cast copper alloy fittings for flared copper tube shall conform to ASME B16.26 and ASTM B 62.  Wrought copper and bronze solder-joint pressure fittings shall conform to ASME B16.22 and ASTM B 75.  Joints and fittings for brazed joint shall be wrought-copper or forged-brass sweat fittings.  Cast sweat-type joints and fittings shall not be allowed for brazed joints.  Brass or bronze adapters for brazed tubing may be used for connecting tubing to flanges and to threaded ends of valves and equipment.

### 2.3.2   Solder

Solder shall conform to ASTM B 32, grade Sb5, tin-antimony alloy for service pressures up to 150 psig.  Solder flux shall be liquid or paste form, non-corrosive and conform to ASTM B 813.

### 2.3.3   Brazing Filler Metal

Filler metal shall conform to AWS A5.8/A5.8M, Type BAg-5 with AWS Type 3 flux, except Type BCuP-5 or BCuP-6 may be used for brazing copper-to-copper joints.

## 2.4   VALVES

Valves shall be designed, manufactured, and tested specifically for refrigerant service.  Valve bodies shall be of brass, bronze, steel, or ductile iron construction.  Valves 1 inch and smaller shall have brazed or socket welded connections.  Threaded end connections shall not be used, except in pilot pressure or gauge lines where maintenance disassembly is required and welded flanges cannot be used.  Internal parts shall be removable for inspection or replacement without applying heat or breaking pipe connections.  Valve stems exposed to the atmosphere shall be stainless steel or corrosion resistant metal plated carbon steel.  Direction of flow shall be legibly and permanently indicated on the valve body.  Control valve inlets shall be fitted with integral or adapted strainer or filter where recommended or required by the manufacturer.  Purge, charge and receiver valves shall be of manufacturer's standard configuration.

### 2.4.1   Refrigerant Stop Valves

Valve shall be the globe or full-port ball type with a back-seating stem especially packed for refrigerant service.  Valve packing shall be replaceable under line pressure.  Valve shall be provided with a wrench operator and a seal cap.  Valve shall be the straight or angle pattern design as indicated.

## 2.5   PIPING ACCESSORIES

### 2.5.1   Filter Driers

Driers shall conform to AHRI 710.  Sizes 5/8 inch and larger shall be the full flow, replaceable core type.  Sizes 1/2 inch and smaller shall be the sealed type.  Cores shall be of suitable desiccant that will not plug, cake, dust, channel, or break down, and shall remove water, acid, and foreign material from the refrigerant.  Filter driers shall be constructed so that none of the desiccant will pass into the refrigerant lines.  Minimum bursting pressure shall be 1,500 psi.

### 2.5.2   Pipe Hangers, Inserts, and Supports

Pipe hangers, inserts, guides, and supports shall conform to MSS SP-58 and MSS SP-69.

### 2.5.3   Escutcheons

Escutcheons shall be chromium-plated iron or chromium-plated brass, either one piece or split pattern, held in place by internal spring tension or set screws.

## 2.6   FABRICATION

### 2.6.1   Factory Coating

Unless otherwise specified, equipment and component items, when fabricated from ferrous metal, shall be factory finished with the manufacturer's standard finish, except that items located outside of buildings shall have weather resistant finishes that will withstand 125 hours exposure to the salt spray test specified in ASTM B 117 using a 5 percent sodium chloride solution.  Immediately after completion of the test, the specimen shall show no signs of blistering, wrinkling, cracking, or loss of adhesion and no sign of rust creepage beyond 1/8 inch on either side of the scratch mark.  Cut edges of galvanized surfaces where hot-dip galvanized sheet steel is used shall be coated with a zinc-rich coating conforming to ASTM D 520, Type I.

### 2.6.2   Factory Applied Insulation

Refrigerant suction lines between the cooler and each compressor shall be insulated with not less than 3/4 inch thick unicellular plastic foam.  Factory insulated items installed outdoors are not required to be fire-rated.  As a minimum, factory insulated items installed indoors shall have a flame spread index no higher than 75 and a smoke developed index no higher than 150.  Factory insulated items (no jacket) installed indoors and which are located in air plenums, in ceiling spaces, and in attic spaces shall have a flame spread index no higher than 25 and a smoke developed index no higher than 50.  Flame spread and smoke developed indexes shall be determined by ASTM E 84.  Insulation shall be tested in the same density and installed thickness as the material to be used in the actual construction.  Material supplied by a manufacturer with a jacket shall be tested as a composite material.  Jackets, facings, and adhesives shall have a flame spread index no higher than 25 and a smoke developed index no higher than 50 when tested in accordance with ASTM E 84.

# PART 3   EXECUTION

## 3.1   EXAMINATION

After becoming familiar with all details of the work, perform a verification of dimensions in the field, and advise the Contracting Officer of any discrepancy before performing any work.

## 3.2   INSTALLATION

Pipe and fitting installation shall conform to the requirements of ASME B31.1.  Pipe shall be cut accurately to measurements established at the jobsite, and worked into place without springing or forcing, completely clearing all windows, doors, and other openings.  Cutting or other weakening of the building structure to facilitate piping installation will not be permitted without written approval.  Pipe or tubing shall be cut square, shall have burrs removed by reaming, and shall permit free expansion and contraction without causing damage to the building structure, pipe, joints, or hangers.

### 3.2.1   Directional Changes

Changes in direction shall be made with fittings, except that bending of pipe 4 inches and smaller will be permitted, provided a pipe bender is used and wide weep bends are formed.  Mitering or notching pipe or other similar construction to form elbows or tees will not be permitted.  The centerline radius of bends shall not be less than 6 diameters of the pipe.  Bent pipe showing kinks, wrinkles, flattening, or other malformations will not be accepted.

### 3.2.2   Functional Requirements

Piping shall be installed 1/2 inch/10 feet of pipe in the direction of flow to ensure adequate oil drainage.  Open ends of refrigerant lines or equipment shall be properly capped or plugged during installation to keep moisture, dirt, or other foreign material out of the system.  Piping shall remain capped until installation.  Equipment piping shall be in accordance with the equipment manufacturer's recommendations and the contract drawings.  Equipment and piping arrangements shall fit into space allotted and allow adequate acceptable clearances for installation, replacement, entry, servicing, and maintenance.

### 3.2.3   Fittings and End Connections

#### 3.2.3.1   Threaded Connections

Threaded connections shall be made with tapered threads and made tight with PTFE tape complying with ASTM D 3308 or equivalent thread-joint compound applied to the male threads only.  Not more than three threads shall show after the joint is made.

#### 3.2.3.2   Brazed Connections

Brazing shall be performed in accordance with AWS BRH, except as modified herein.  During brazing, the pipe and fittings shall be filled with a pressure regulated inert gas, such as nitrogen, to prevent the formation of scale.  Before brazing copper joints, both the outside of the tube and the inside of the fitting shall be cleaned with a wire fitting brush until the entire joint surface is bright and clean.  Brazing flux shall not be used.  Surplus brazing material shall be removed at all joints.  Steel tubing joints shall be made in accordance with the manufacturer's recommendations.  Joints in steel tubing shall be painted with the same material as the baked-on coating within 8 hours after joints are made.  Tubing shall be protected against oxidation during brazing by continuous purging of the inside of the piping using nitrogen.  Piping shall be supported prior to brazing and not be sprung or forced.

### 3.2.4   Valves

#### 3.2.4.1   General

Refrigerant stop valves shall be installed on each side of each piece of equipment such as compressors condensers, evaporators, receivers, and other similar items in multiple-unit installation, to provide partial system isolation as required for maintenance or repair.  Stop valves shall be installed with stems horizontal unless otherwise indicated.  Ball valves shall be installed with stems positioned to facilitate operation and maintenance.  Isolating valves for pressure gauges and switches shall be external to thermal insulation.  Safety switches shall not be fitted with isolation valves.  Filter dryers having access ports may be considered a point of isolation.  Purge valves shall be provided at all points of systems where accumulated noncondensable gases would prevent proper system operation.  Valves shall be furnished to match line size, unless otherwise indicated or approved.

### 3.2.5   Filter Dryer

A liquid line filter dryer shall be provided on each refrigerant circuit located such that all liquid refrigerant passes through a filter dryer.  Dryers shall be sized in accordance with the manufacturer's recommendations for the system in which it is installed.  Dryers shall be installed such that it can be isolated from the system, the isolated portion of the system evacuated, and the filter dryer replaced.  Dryers shall be installed in the horizontal position except replaceable core filter dryers may be installed in the vertical position with the access flange on the bottom.

### 3.2.6   Pipe Hangers, Inserts, and Supports

Pipe hangers, inserts, and supports shall conform to MSS SP-58 and MSS SP-69, except as modified herein.  Pipe hanger types 5, 12, and 26 shall not be used.  Hangers used to support piping 2 inches and larger shall be fabricated to permit adequate adjustment after erection while still supporting the load.  Piping subjected to vertical movement, when operating temperatures exceed ambient temperatures, shall be supported by variable spring hangers and supports or by constant support hangers.

#### 3.2.6.1   Hangers

Type 3 shall not be used on insulated piping.  Type 24 may be used only on trapeze hanger systems or on fabricated frames.

#### 3.2.6.2   Angle Attachments

Type 20 attachments used on angles and channels shall be furnished with an added malleable-iron heel plate or adapter.

#### 3.2.6.3   Saddles and Shields

Where Type 39 saddle or Type 40 shield are permitted for a particular pipe attachment application, the Type 39 saddle, connected to the pipe, shall be used on all pipe 4 inches and larger when the temperature of the medium is 60 degrees F or higher.  Type 40 shields shall be used on all piping less than 4 inches and all piping 4 inches and larger carrying medium less than 60 degrees F.  A high density insulation insert of cellular glass shall be used under the Type 40 shield for piping 2 inches and larger.

#### 3.2.6.4   Horizontal Pipe Supports

Horizontal pipe supports shall be spaced as specified in MSS SP-69 and a support shall be installed not over 1 foot from the pipe fitting joint at each change in direction of the piping.  Pipe supports shall be spaced not over 5 feet apart at valves.  Pipe hanger loads suspended from steel joist with hanger loads between panel points in excess of 50 pounds shall have the excess hanger loads suspended from panel points.

#### 3.2.6.5   Vertical Pipe Supports

Vertical pipe shall be supported at each floor, except at slab-on-grade, and at intervals of not more than 15 feet not more than 8 feet from end of risers, and at vent terminations.

#### 3.2.6.6   Pipe Guides

Type 35 guides using, steel, reinforced polytetrafluoroethylene (PTFE) or graphite slides shall be provided where required to allow longitudinal pipe movement.  Lateral restraints shall be provided as required.  Slide materials shall be suitable for the system operating temperatures, atmospheric conditions, and bearing loads encountered.

#### 3.2.6.7   Multiple Pipe Runs

In the support of multiple pipe runs on a common base member, a clip or clamp shall be used where each pipe crosses the base support member.  Spacing of the base support members shall not exceed the hanger and support spacing required for an individual pipe in the multiple pipe run.

### 3.2.7   Pipe Alignment Guides

Pipe alignment guides shall be provided where indicated for expansion loops, offsets, and bends and as recommended by the manufacturer for expansion joints, not to exceed 5 feet on each side of each expansion joint, and in lines 4 inches or smaller not more than 2 feet on each side of the joint.

### 3.2.8   Pipe Anchors

Anchors shall be provided wherever necessary or indicated to localize expansion or to prevent undue strain on piping.  Anchors shall consist of heavy steel collars with lugs and bolts for clamping and attaching anchor braces, unless otherwise indicated.  Anchor braces shall be installed in the most effective manner to secure the desired results using turnbuckles where required.  Supports, anchors, or stays shall not be attached where they will injure the structure or adjacent construction during installation or by the weight of expansion of the pipeline.  Where pipe and conduit penetrations of vapor barrier sealed surfaces occur, these items shall be anchored immediately adjacent to each penetrated surface, to provide essentially zero movement within penetration seal.  Detailed drawings of pipe anchors shall be submitted for approval before installation.

### 3.2.9   Building Surface Penetrations

Sleeves shall not be installed in structural members except where indicated or approved.  Sleeves in nonload bearing surfaces shall be galvanized sheet metal, conforming to ASTM A 653/A 653M, Coating Class G-90, 20 gauge.  Sleeves in load bearing surfaces shall be uncoated carbon steel pipe, conforming to ASTM A 53/A 53M, Schedule 30 Standard weight.  Sealants shall be applied to moisture and oil-free surfaces and elastomers to not less than 1/2 inch depth.  Sleeves shall not be installed in structural members.

#### 3.2.9.1   Escutcheons

Finished surfaces where exposed piping, bare or insulated, pass through floors, walls, or ceilings, except in boiler, utility, or equipment rooms, shall be provided with escutcheons.  Where sleeves project slightly from floors, special deep-type escutcheons shall be used.  Escutcheon shall be secured to pipe or pipe covering.

### 3.2.10   Field Applied Insulation

Field installed insulation shall be as specified in Section 23 07 00 THERMAL INSULATION FOR MECHANICAL SYSTEMS, except as defined differently herein.

## 3.3   CLEANING AND ADJUSTING

Clean uncontaminated system(s) by evacuation and purging procedures currently recommended by refrigerant and refrigerant equipment manufacturers, and as specified herein, to remove small amounts of air and moisture.  Systems containing moderate amounts of air, moisture, contaminated refrigerant, or any foreign matter shall be considered contaminated systems.  Restoring contaminated systems to clean condition including disassembly, component replacement, evacuation, flushing, purging, and re-charging, shall be performed using currently approved refrigerant and refrigeration manufacturer's procedures.  Restoring contaminated systems shall be at no additional cost to the Government as determined by the Contracting Officer.  Water shall not be used in any procedure or test.

## 3.4   REFRIGERANT PIPING TESTS

After all components of the refrigerant system have been installed and connected, subject the entire refrigeration system to pneumatic, evacuation, and startup tests as described herein.  Conduct tests in the presence of the Contracting Officer's Representative.  Water and electricity required for the tests will be furnished by the Government.  Provide all material, equipment, instruments, and personnel required for the test.  Provide the services of a qualified technician, as required, to perform all tests and procedures indicated herein.  Field tests shall be coordinated with Section 23 05 93 TESTING, ADJUSTING, AND BALANCING OF HVAC SYSTEMS.

### 3.4.1   Preliminary Procedures

Prior to pneumatic testing, equipment which has been factory tested and refrigerant charged as well as equipment which could be damaged or cause personnel injury by imposed test pressure, positive or negative, shall be isolated from the test pressure or removed from the system.  Safety relief valves and rupture discs, where not part of factory sealed systems, shall be removed and openings capped or plugged.

### 3.4.2   Pneumatic Test

Pressure control and excess pressure protection shall be provided at the source of test pressure.  Valves shall be wide open, except those leading to the atmosphere.  Test gas shall be dry nitrogen, with minus 70 degree F dew point and less than 5 ppm oil.  Test pressure shall be applied in two stages before any refrigerant pipe is insulated or covered.  First stage test shall be at 10 psi with every joint being tested with a thick soap or color indicating solution.  Second stage tests shall raise the system to the minimum refrigerant leakage test pressure specified in ANSI/ASHRAE 15 & 34 with a maximum test pressure 25 percent greater.  Pressure above 100 psig shall be raised in 10 percent increments with a pressure acclimatizing period between increments.  The initial test pressure shall be recorded along with the ambient temperature to which the system is exposed.  Final test pressures of the second stage shall be maintained on the system for a minimum of 24 hours.  At the end of the 24 hour period, the system pressure will be recorded along with the ambient temperature to which the system is exposed.  A correction factor of 0.3 psi will be allowed for each degree F change between test space initial and final ambient temperature, plus for increase and minus for a decrease.  If the corrected system pressure is not exactly equal to the initial system test pressure, then the system shall be investigated for leaking joints.  To repair leaks, the joint shall be taken apart, thoroughly cleaned, and reconstructed as a new joint.  Joints repaired by caulking, remelting, or back-welding/brazing shall not be acceptable.  Following repair, the entire system shall be retested using the pneumatic tests described above.  The entire system shall be reassembled once the pneumatic tests are satisfactorily completed.

### 3.4.3   Evacuation Test

Following satisfactory completion of the pneumatic tests, the pressure shall be relieved and the entire system shall be evacuated to an absolute pressure of 300 micrometers.  During evacuation of the system, the ambient temperature shall be higher than 35 degrees F.  No more than one system shall be evacuated at one time by one vacuum pump.  Once the desired vacuum has been reached, the vacuum line shall be closed and the system shall stand for 1 hour.  If the pressure rises over 500 micrometers after the 1 hour period, then the system shall be evacuated again down to 300 micrometers and let set for another 1 hour period.  The system shall not be charged until a vacuum of at least 500 micrometers is maintained for a period of 1 hour without the assistance of a vacuum line.  If during the testing the pressure continues to rise, check the system for leaks, repair as required, and repeat the evacuation procedure.  During evacuation, pressures shall be recorded by a thermocouple-type, electronic-type, or a calibrated-micrometer type gauge.

### 3.4.4   System Charging and Startup Test

Following satisfactory completion of the evacuation tests, the system shall be charged with the required amount of refrigerant by raising pressure to normal operating pressure and in accordance with manufacturer's procedures.  Following charging, the system shall operate with high-side and low-side pressures and corresponding refrigerant temperatures, at design or improved values.  The entire system shall be tested for leaks.  Fluorocarbon systems shall be tested with halide torch or electronic leak detectors.

### 3.4.5   Refrigerant Leakage

If a refrigerant leak is discovered after the system has been charged, the leaking portion of the system shall immediately be isolated from the remainder of the system and the refrigerant pumped into the system receiver or other suitable container.  Under no circumstances shall the refrigerant be discharged into the atmosphere.

### 3.4.6   Contractor's Responsibility

At all times during the installation and testing of the refrigeration system, take steps to prevent the release of refrigerants into the atmosphere.  The steps shall include, but not be limited to, procedures which will minimize the release of refrigerants to the atmosphere and the use of refrigerant recovery devices to remove refrigerant from the system and store the refrigerant for reuse or reclaim.  At no time shall more than 3 ounces of refrigerant be released to the atmosphere in any one occurrence.  Any system leaks within the first year shall be repaired in accordance with the requirements herein at no cost to the Government including material, labor, and refrigerant if the leak is the result of defective equipment, material, or installation.

-- End of Section --

SECTION 23 81 00

VARIABLE REFRIGERANT FLOW SYSTEM

PART 1 GENERAL

The Bidding and Contract Requirements, Division 1 General Requirements, Section 23 00 00 AIR SUPPLY, DISTRIBUTION, VENTILATION, AND EXHAUST SYSTEMS, and Section 23 03 00 BASIS MECHANICAL MATERIALS AND METHODS shall apply to this section.

  - SCOPE OF WORK

The work covered under this section shall include the following:

- Complete variable refrigerant flow system including equipment, piping, and controls. System shall be a VRF (variable refrigerant flow) multi split air conditioning system. The system will utilize an air cooled condensing unit supplying a maximum of forty indoor fan coil units with combinations of outdoor units 3 - 12 ton capacity with a maximum of 2 outdoor units connected at one time.

- The VRF (Variable Refrigerant Flow) system shall be a simultaneous cooling and heating heat pump system. The VRF system shall consist of an outdoor unit, high efficiency heat recovery units designed for minimum piping and maximum design flexibility, indoor units, and controls by the equipment manufacturer. Each indoor unit shall be independently capable of operating in either heating or cooling mode regardless of the mode of other indoor units.

- The variable refrigerant flow system piping system shall be installed by a manufacturer's certified contractor.

- The installing contractor shall be trained and certified at the manufacturer's training facility prior to installation, startup, and commissioning. Submit for review the installation contractor's certification from the manufacturer. This certification shall include the company certification as well as individual certifications for each contractor which will be working on this project.

E. 	The refrigeration piping system shall be provided, installed, tested, evacuated, and charged.

1.2 	QUALITY ASSURANCE

- Manufacturers Field Service Engage a factory-authorized service representative to inspect field assembled components and equipment installation, including connections, and to assist in field testing.

- The units shall be listed by Electrical Laboratories (ETL) and bear the ETL label. All wiring shall be in accordance with the National Electrical Code (NEC). The units shall be manufactured in a facility registered to ISO 9001 and ISO14001.

- The refrigeration piping system shall be provided, installed, tested, evacuated and charged in accordance with the manufacturer's recommendations, ANSI, ASHRAE, and ARI's Safety Code for Mechanical Refrigeration, state and local codes.

- Perform the following field tests and inspections and prepare test reports:

- Leak Test After installation, charge system and test for leaks. Repair leaks 	and retest until no leaks exist.

- Operational Test After electrical circuitry has been energized, start units to 	confirm proper motor rotation and unit operation.

- Test and adjust controls and safeties. Replace damaged and 	malfunctioning controls and equipment.

E.	Remove and replace malfunctioning units and retest as specified above.

## 1.3 	SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-03 Product Data

Manufacturer’s standard catalog data highlighted to show material, size, options, performance charts and curves, etc. in adequate detail to demonstrate compliance with contract requirements.  Include in the data manufacturer’s recommended installation instructions and procedures.  Provide data for the following components as a minimum:

Outdoor Heat Pump Units

Indoor Fan Coil Units

Branch Controllers

Controls

SD-07 Certificates

Contractor Qualifications

SD-10 Operation and Maintenance Data

List of Units to be Included in O&M Manuals

PART 2 PRODUCTS

2.1 	REFRIGERANT COMPONENTS

A. 	The equipment specified in this section shall operate with refrigerant R410A, no exceptions or substitutions.

B. 	The system shall utilize fully modulating electronic expansion valves.

C. 	Refrigerant Piping

- The refrigerant piping system shall be provided complete and installed in accordance with the manufacturer's recommendations and as specified herein. The size of the refrigerant pipes shall be obtained from the equipment manufacturer unless otherwise shown on the drawings.

- Pipe, Fittings, and Accessories:  The pipe shall be type ACR 'L' hard drawn copper refrigerant tubing with hard wrought copper fittings. All of the joints shall be brazed with a filler material that complies with AWS classification BCuP 5. A sight glass with moisture indicator shall be provided if not provided with equipment. Use type 'L' copper tubing to pipe the relief valve discharge to the outside.

- Condensate Drain Piping:  Shall be type 'L' copper tubing.

- The system shall be capable of operating with refrigerant piping up to 492 equivalent feet, a total combined length of 984 feet of piping between the condensing and fan coil units with 164 feet maximum vertical difference, without any oil traps or additional equipment. The vertical difference shall not exceed a maximum of 131 feet where the outdoor unit is located below the indoor unit.

2.2 HEAT RECOVERY UNITS FOR SIMULTANEOUS HEATING AND COOLING SYSTEMS

A. 	General:  The Heat Recovery Unit shall be designed for use with VRF equipment of the same manufacturer. These units shall be equipped with a circuit board that interfaces to the controls system and shall perform all functions necessary for operation. The unit shall have a galvanized steel finish. The heat recovery unit shall be completely factory assembled, piped, and wired. Each unit shall be run tested at the factory. This unit shall be mounted indoors. The sum of connected capacity of all indoor air handlers shall range from 50% to 150% of rated capacity.

B.	 Unit Cabinet

- The casing shall be fabricated of galvanized steel.

- Each cabinet shall house a liquid-gas separator and multiple refrigeration control valves.

- The unit shall house tube-in-tube heat exchangers.

C. 	Refrigerant R410A refrigerant shall be required for Heat Recovery units in conjunction with outdoor unit systems.

D. 	Refrigerant Valves

- The unit shall be furnished with multiple branch circuits which can individually accommodate up to 54,000 BTUH and/or three indoor units. Branches may be twinned to allow more than 54,000 BTUH.

- Each branch shall have multiple two-position valves to control refrigerant flow for optimum efficiency.

- Service shutoff valves shall be installed for each branch to allow service to any indoor unit without field interruption to overall system operation. Shutoff valves 	shall be full-port ball valves, rated at 700 PSIG, with a Schrader port.

- Linear electronic expansion valves shall be used to control the variable refrigerant flow.

E.	 Integral Drain Pan:  An integral condensate pan and drain, if required, shall be provided.

F. 	Electrical

- The unit electrical power shall be 208/230 volts, 1 phase, 60 hertz.

- The unit shall be capable of satisfactory operation within voltage limits of 	(208V/60Hz).

- The Heat Recovery unit shall be controlled by integral microprocessors.

- The control circuit between the indoor units and the outdoor unit shall be 	24VDC completed using a 2conductor, twisted pair shielded cable to 	provide total integration of the system.

2.3 INDOOR AIR HANDLING UNITS

A. 	It shall be possible for the total connected capacity of the indoor units to be between 50 and 130% of the capacity of the outdoor unit.

B. 	Each indoor unit will have a heat exchanger which shall be constructed from copper tubing with aluminum fins. The flow of refrigerant through the heat exchanger will be controlled by an electronic proportional expansion valve. This valve will be controlled by two pipe thermistors, a return air and discharge air thermistor and shall be capable of controlling the variable capacity of the indoor unit between 25% and 100%.

C. 	Each indoor unit shall have an operating voltage of 208-230V/1 phase/60Hz. The indoor unit shall supply demand capacity information to the outdoor unit via its control algorithm.

D. 	Construction

- The indoor unit shall be completely factory assembled and tested. The unit shall include factory wiring, piping, electronic proportional expansion valve, control circuit board, fan motor thermal protector, condensate drain pan, self-diagnostics, auto-restart function, 3minute fused time delay, and test run switch.

- The indoor unit shall be equipped with a condensate pan.

- Coil

- Coils shall be of the direct expansion type constructed from copper tubes expanded into aluminum fins to form a mechanical bond.

- A condensate pan shall be located under the coil.  The condensate pan shall have a built in high level safety alarm to shut down the unit.

3. 	A thermistor shall be located on the liquid and gas line.

2.4 	CONTROLS

- The units shall have controls provided with the unit by the manufacturer to perform input functions necessary to operate the system.

B. 	Computerized PID control shall be used to maintain room temperature within 1F of setpoint.

C.	Control sensors, bacnet card and intelligent controller shall conform to the equipment schedules on the mechanical design drawings.

2.5 	CONTROLLERS

- Physical Characteristics:  The control system shall be a neutral color plastic material with a Liquid Crystal Display (LCD).

- Electrical Characteristics

- General:  From each circuit board to the controls, the electrical voltage shall be 16 24 volts DC.

- Wiring:  Control wiring shall be installed in a daisy chain configuration from indoor unit to indoor unit then to the outdoor unit.  Control wiring shall run from the indoor unit terminal block to the specific controller for that unit.

- Wiring Size:  The wire shall be a shielded, size AWG162 or AWG 182.

- Individual Zone Controller B Simplified Wired Remote Controller

1. 	The simplified wired remote controller shall be able to control 1 Zone.

2. 	The simplified wired remote controller shall have the following features:

- Operation:  Start/Stop, Operation Mode, Temperature Setting, 60F 90F Set Point Range, Fan Speed, Airflow Direction.

- Monitoring:  Status, malfunction flashing, malfunction content, filter sign, operation mode, temperature setting, permit/prohibit selection, fan speed, airflow direction.

- Scheduling:  ON/OFF Timer.

d. Control Management:  Field Setting Mode, Group Setting, Auto Restart.

D. 	System Remote Controller:  The controller shall control up to 11 units in 4 zones and shall be able to be used in conjunction with all room controller types.  Collective and individual group commands are available with permit/prohibit individual remote controller function.  The system controller shall use the following connections for power and remote monitoring:

L1: Power supply (60 Hz, 208230 VAC)

C1: Inter-unit control wiring (Low voltage)

C3: Auxiliary

C4: Ground for inter-unit control wiring

A1: Input for turning ON air conditioners concurrently

A2: Input for turning OFF air conditioners concurrently

A3: Common input for turning air conditioners ON or OFF

B1: On operation state indicator output

B2: Alarm indicator output

B3: Common indicator output

E. 	Web Enabled Intelligent Controller

1. 	This controller shall be wall mounted and hard wired. It will be manufactured with an LCD display and will be the manufacturers’ standard color. The controller will be capable of individually controlling the following functions on at least 50 indoor fan coil units:

a. 	On/off.

b. 	Operating mode.

c. 	Set point.

d. 	Fan speed.

e. 	Louver position.

f. 	Timer settings.

g. 	Test run.

2. 	The controller shall also be capable of displaying the following information 	individually for at least 50 indoor fan coil units:

a. 	On/off.

b. 	Operating mode.

c. 	Set point.

d. 	Fan speed.

e. 	Louver position.

f. 	Timer settings.

g. 	Test run.

h. 	Fault diagnosis.

3. 	Each Intelligent controller unit shall be accessed both locally and remotely via standard Internet Explorer IE6 or IE7 software. The Intelligent controller will be able to indicate system alarms via volt free contacts as well as providing control points for other DO devices. Additionally, the intelligent controller shall be able to monitor individual usage of heating and cooling demands, report alarm and conditions to nominated email address, and enable remote alteration of systems setpoints and schedules.

PART 3 EXECUTION

3.1 	INSTALLATION

- Install all piping, fittings, and insulation to meet manufacturers’ requirements. Install units level and plumb. Evaporator fan components shall be installed using manufacturers standard mounting devices securely fastened to building structure. Install and connect refrigerant tubing and fittings.

- Installer shall supply isolation ball valves for zoned refrigerant isolation. Installer shall supply Isolation ball valves with Schrader connection for isolating refrigerant charge and evacuation at each connected air handling unit and condensing unit. Isolation ball valves, with Schrader connection, are required for instances of air handling unit isolation for troubleshooting, repair, or replacement without affecting the remainder of the system. Isolation ball valves with Schrader connection are also required at condensing unit connection to isolate unit for troubleshooting, repair or replacement and as required to provide partial capacity Heating/Cooling in the instance of a failure of one of the multiple outdoor unit (condensing unit) compressors.

C. 	During brazing an inert gas (such as nitrogen) shall be continuously passed through the system at a rate sufficient to maintain an oxygen free environment to prevent the formation of copper oxide scale. After piping has been completed, the refrigerant piping system shall be pressure tested at a pressure of 300 psi on the high side and 150 psi on the low side. The pressure shall be maintained on the system for a minimum of 12 hours. The system shall be evacuated when the surrounding ambient air is not less than 60 F. If the temperature is less, auxiliary heat must be provided to insure proper evacuating conditions. A minimum vacuum of 500 Microns of Hg. shall be pulled on the system and maintained for 12 hours. The vacuum pump displacement shall be not less than 2 cfm for up to 15 tons. The system shall be charged as recommended by the equipment manufacturer.

D. 	Start Up Engage manufacturer or factory authorized service representative to perform startup service. Manufacturer shall provide onsite startup and commissioning assistance through job completion. Complete installation and startup checks according to manufacturers’ written instructions. This shall include a factory startup for factory provided control devices as well as configuring control points for other DO devices. Service representative shall completely configure all control devices and establish remote internet connectivity with the owner’s energy management department web server.

E. 	Demonstration:  Engage manufacturer or factory authorized service representative to train Owners maintenance personnel to adjust, operate and maintain individual units and complete system. This shall include training of the owner’s energy management department representatives as to establish control system programming, scheduling routines, alarm reporting, system topography, communication protocols and password level assignments.

F. 	The indoor air handling and outside condensing units shall be installed in accordance with the manufacturer's recommendations and as shown on the drawings. The first unit installed will be considered the typical mock up and shall require notification, inspection and approval by the designated owner representative and/or architect and engineer before any additional installations will be allowed.

G. 	Provide a typed list of all the different units, their filter sizes, and belt sizes to be included in the O&M manuals. The list shall include the unit designation, filter size, belt size, and the number of filters and belts required for each unit. In addition to this, submit to the Contracting Officer two additional copies of the list.

-- END OF SECTION –

SECTION 23 81 01

UNITARY AIR CONDITIONING EQUIPMENT

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to within the text by the basic designation only.

AIR-CONDITIONING, HEATING AND REFRIGERATION INSTITUTE (AHRI)

AHRI DCUP	(Online) Directory of Certified Unitary Products

AMERICAN SOCIETY OF HEATING, REFRIGERATING AND AIR-CONDITIONING ENGINEERS (ASHRAE)

ANSI/ASHRAE 15 & 34	(2013; Addenda A 2014; ERTA 1 2014; Addenda A-T AND SUPP 2015; ERTA 2 2015; INT 1 2015; ERTA 3 2015; ERTA 4 2016; INT 2-3 2016) ANSI/ASHRAE Standard 15-Safety Standard for Refrigeration Systems and ANSI/ASHRAE Standard 34-Designation and Safety Classification of Refrigerants

ASHRAE 52.2	(2012; Errata 1  2013; INT 1 2014;  ADD A, B, AND D SUPP 2015; INT 3 2015; Errata 2 2015; ADD C 2015; ADD E, F 2016) Method of Testing General Ventilation Air-Cleaning Devices for Removal Efficiency by Particle Size

ASHRAE 55	(2010) Thermal Environmental Conditions for Human Occupancy

ASHRAE 62.1	(2010; Errata 2011; INT 3 2012; INT 4 2012; INT 5 2013) Ventilation for Acceptable Indoor Air Quality

ASTM INTERNATIONAL (ASTM)

ASTM A123/A123M	(2013) Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products

ASTM B117	(2016) Standard Practice for Operating Salt Spray (Fog) Apparatus

ASTM D1654	(2008) Evaluation of Painted or Coated Specimens Subjected to Corrosive Environments

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

NEMA ICS 1	(2000; R 2015) Standard for Industrial Control and Systems: General Requirements

NEMA ICS 2	(2000; R 2005; Errata 2008) Standard for Controllers, Contactors, and Overload Relays Rated 600 V

NEMA ICS 6	(1993; R 2011) Enclosures

NEMA MG 1	(2016) Motors and Generators

U.S. DEPARTMENT OF ENERGY (DOE)

Energy Star	(1992; R 2006) Energy Star Energy Efficiency Labeling System (FEMP)

UNDERWRITERS LABORATORIES (UL)

UL 873	(2007; Reprint Feb 2015) Standard for Temperature-Indicating and -Regulating Equipment

UL 900	(2015) Standard for Air Filter Units

## 1.2   RELATED REQUIREMENTS

Section 23 03 00 BASIC MECHANICAL MATERIALS AND METHODS, applies to this section with the additions and modifications specified herein.

## 1.3   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-02 Shop Drawings

Control System Wiring Diagrams

SD-03 Product Data

Packaged Air Conditioning Unit

Include documentation for Energy Star qualifications or meeting FEMP requirements.  Indicate Energy Efficiency Rating.

Filters

Thermostats

Refrigerant

Provide MSDS sheets for all refrigerants

SD-06 Test Reports

Salt-Spray Tests

Start-Up and Initial Operational Tests

SD-08 Manufacturer's Instructions

Packaged Air Conditioning Unit

Filters

Thermostats

SD-10 Operation and Maintenance Data

Air Conditioners

Filters

Thermostats

## 1.4   QUALITY ASSURANCE

### 1.4.1   Modification of References

Accomplish work in accordance with the referenced publications, except as modified by this section.  Consider the advisory or recommended provisions to be mandatory, as though the word "shall" had been substituted for the words "should" or "could" or "may," wherever they appear.  Interpret reference to "the Authority having jurisdiction," "the Administrative Authority," "the Owner," or "the Design Engineer" to mean the Contracting Officer.

### 1.4.2   Detail Drawing

For refrigerant piping, submit piping, including pipe sizes.  Submit control system wiring diagrams.

### 1.4.3   Safety

Design, manufacture, and installation of unitary air conditioning equipment shall conform to ANSI/ASHRAE 15 & 34.

### 1.4.4   Posted Operating Instructions

Submit posted operating instructions for each packaged air conditioning unit.

### 1.4.5   Sizing

Size equipment based on Design Manual CS from the Air Conditioning Contractors of America; do not oversize.

## 1.5   REFRIGERANTS

Refrigerants shall have an Ozone Depletion Potential (ODP) of 0.0.  The ODP shall be in accordance with the "Montreal Protocol On Substances That Deplete The Ozone Layer," September 1987, sponsored by the United Nations Environment Programme.  CFCs and HCFCs and Halons shall not be permitted.  Refrigerant shall be an approved alternative refrigerant per EPA's Significant New Alternative Policy (SNAP) listing.

## 1.6   ENVIRONMENTAL REQUIREMENTS

For proper Indoor Environmental Quality, maintain positive pressure within the building.  Ventilation shall meet or exceed ASHRAE 62.1 and all published addenda.  Meet or exceed filter media efficiency as tested in accordance with ASHRAE 52.2.  Thermal comfort shall meet or exceed ASHRAE 55.

# PART 2   PRODUCTS

## 2.1   AIR CONDITIONERS

### 2.1.1   Single Package Type

Provide factory packaged combination heating and cooling units.  Provide units suitable for outdoor installation.  Provide units with suitable lifting attachments, remote control panel.  List units with capacities smaller than 135,000 Btu/hr in the AHRI DCUP; in lieu of listing in the AHRI Directory, a letter of certification from AHRI that the units have been certified and will be listed in the next Directory will be acceptable.  Provide capacity, electrical characteristics, and operating conditions as indicated.  Condensers shall provide not less than 10 degrees F liquid subcooling at standard ratings.  Air conditioners must include the Energy Star label affixed to the equipment.

### 2.1.2   Heaters

Provide as an integral part of the evaporator-blower unit.  Provide electric open coils.

.

### 2.1.3   Compressors

Capacity reduction may be accomplished by cylinder unloading, use of multi- or variable speed compressors, use of multiple, but not more than four compressors, or a combination of the two methods.  Units with cylinder unloading shall start with capacity reduction devices in the unloaded position.  Units with multiple compressors shall have means to sequence starting of compressors.  Provide compressors with devices to prevent short cycling when shut down by safety controls.  Device shall delay operation of compressor motor for at least 3 minutes but not more than 6 minutes.   Provide reciprocating compressors with crankcase heaters in accordance with the manufacturer's recommendations.  If compressors are paralleled, provide not less than two independent circuits.

### 2.1.4   Coils

On coils with all-aluminum construction, provide tubes of aluminum alloy 1100, 1200, or 3102; provide fins of aluminum alloy 7072; and provide tube sheets of aluminum alloy 7072 or 5052.  Provide a separate air cooled condenser circuit for each compressor or parallel compressor installation.

### 2.1.5   Condenser Controls

Provide start-up and head pressure controls to allow for system operation at ambient temperatures down to -8 degrees F.

### 2.1.6   Fans

Provide belt-driven evaporator fans with adjustable pitch pulleys; except for units less than 5 ton capacity, direct drive with at least two speed taps may be used.  Select pulleys at approximately midpoint of the adjustable range.

### 2.1.7   Filters

Provide filters of the type specified in this section.

### 2.1.8   Thermostats

Provide adjustable type that conforms to applicable requirements of UL 873.  Provide combination heating-cooling type with contacts hermetically sealed against moisture, corrosion, lint, dust, and foreign material. Design to operate on not more than 1.5 degrees F differential and of suitable range calibrated in degrees F.  Provide adjustable heat anticipation and fixed cooling anticipation.  Provide two independent temperature sensing elements electrically connected to control the compressor and heating equipment, respectively.  Accomplish manual switching for system changeover from heating to cooling or cooling to heating and fan operation through the use of a thermostat subbase.  Provide system selector switches to provide "COOL" and "OFF" and "HEAT" and fan selector switches to provide "AUTOMATIC" and "ON."  Provide relays, contactors, and transformers located in a panel or panels for replacement and service.

#### 2.1.8.1   Cooling

a.  When thermostat is in "COOL" position with fan selector switch in "AUTO" position, compressor, evaporator fan, and condenser fan shall cycle together.

b.  When thermostat is in "COOL" position with fan selector switch in "ON" position, compressor, and condenser fan shall cycle together and evaporator fan shall run continuously.

#### 2.1.8.2   Heating

a.  When thermostat is in "HEAT" position with fan selector switch in "AUTO" position, heater and supply air fan shall cycle together. Provide a separate thermostat to keep the fan running until the heater cools.

b.  When thermostat is in "HEAT" position with fan selector switch in "ON" position, heater shall cycle and supply air fan shall run continuously.

#### 2.1.8.3   Supply Air Fan

a.  When fan selector switch is in "AUTO" position with thermostat in "OFF" position, fan shall not run.

b.  When fan selector switch is in "ON" position, fan shall run continuously.

## 2.2   FILTERS

Provide filters to filter outside air and return air and locate inside air conditioners.  Provide replaceable (throw-away) type.  Filters shall conform to UL 900, Class 1 or Class 2.  Polyurethane filters shall not be used on units with multiframe filters.

### 2.2.1   Replaceable Type Filters

Throw-away frames and media, standard dust holding capacity, 350 fpm maximum face velocity, and 2 inches thick.  Filters shall have a minimum efficiency reporting value (MERV) of 8 when tested in accordance with ASHRAE 52.2.

## 2.3   MOTORS AND STARTERS

NEMA MG 1, NEMA ICS 1, and NEMA ICS 2.  Variable speed.  Motors less than 1 hp shall meet NEMA High Efficiency requirements.  Motors 1 hp and larger shall meet NEMA Premium Efficiency requirements.  Determine specific motor characteristics to ensure provision of correctly sized starters and overload heaters.  Provide motors to operate at full capacity with a voltage variation of plus or minus 10 percent of the motor voltage rating. Motor size shall be sufficient for the duty to be performed and shall not exceed its full load nameplate current rating when driven equipment is operated at specified capacity under the most severe conditions likely to be encountered.  When motor size provided differs from size indicated or specified, the Contractor shall make the necessary adjustments to the wiring, disconnect devices, and branch circuit protection to accommodate equipment actually provided.  Provide weather-resistant, watertight type starter enclosures in accordance with NEMA ICS 6.

## 2.4   FINISHES

Provide steel surfaces of equipment including packaged terminal units, heat pumps, and air conditioners, that do not have a zinc coating conforming to ASTM A123/A123M, or a duplex coating of zinc and paint, with a factory applied coating or paint system.  Provide a coating or paint system on actual equipment identical to that on salt-spray test specimens with respect to materials, conditions of application, and dry-film thickness.

## 2.5   SOURCE QUALITY CONTROL

### 2.5.1   Salt-Spray Tests

Salt-spray test the factory-applied coating or paint system of equipment including packaged terminal units, heat pumps, and air conditioners in accordance with ASTM B117.  Conduct test for 500 hours for equipment installed outdoors, or 125 hours for equipment installed indoors.  Test specimens shall have a standard scribe mark as defined in ASTM D1654.  Upon completion of exposure, evaluate and rate the coating or paint system in accordance with procedures A and B of ASTM D1654.  Rating of failure at the scribe mark shall not be less than six, average creepage not greater than 1/8 inch.  Rating of the unscribed area shall not be less than 10, no failure.

# PART 3   EXECUTION

## 3.1   EQUIPMENT INSTALLATION

Install equipment and components in a manner to ensure proper and sequential operation of equipment and equipment controls.  Install equipment not covered in this section, or in manufacturer's instructions, as recommended by manufacturer's representative.  Provide proper foundations for mounting of equipment, accessories, appurtenances, piping and controls including, but not limited to, supports, vibration isolators, stands, guides, anchors, clamps and brackets.  Foundations for equipment shall conform to equipment manufacturer's recommendation, unless otherwise indicated.  Set anchor bolts and sleeves using templates.  Provide anchor bolts of adequate length, and provide with welded-on plates on the head end embedded in the concrete.  Level equipment bases, using jacks or steel wedges, and neatly grout-in with a nonshrinking type of grouting mortar. Locate equipment to allow working space for servicing including shaft removal, disassembling compressor cylinders and pistons, replacing or adjusting drives, motors, or shaft seals, access to water heads and valves of shell and tube equipment, tube cleaning or replacement, access to automatic controls, refrigerant charging, lubrication, oil draining and working clearance under overhead lines.  Provide electric isolation between dissimilar metals for the purpose of minimizing galvanic corrosion.

### 3.1.1   Unitary Air Conditioning System

Install as indicated, in accordance with requirements of ANSI/ASHRAE 15 & 34, and the manufacturer's installation and operational instructions.

## 3.2   ACCESS PANELS

Provide access panels for concealed valves, controls, dampers, and other fittings requiring inspection and maintenance.

## 3.3   AIR FILTERS

Allow access space for servicing filters.  Install filters with suitable sealing to prevent bypassing of air.

## 3.4   FLASHING AND PITCH POCKETS

Provide flashing and pitch pockets for equipment supports and roof penetrations and flashing where piping or ductwork passes through exterior walls.

## 3.5   IDENTIFICATION TAGS AND PLATES

Provide equipment, gages, thermometers, valves, and controllers with tags numbered and stamped for their use.  Provide plates and tags of brass or suitable nonferrous material, securely mounted or attached.  Provide minimum letter and numeral size of 1/8 inch high.

## 3.6   FIELD QUALITY CONTROL

### 3.6.1   Leak Testing

Upon completion of installation of air conditioning equipment, test factory- and field-installed refrigerant piping with an electronic-type leak detector.  Use same type of refrigerant to be provided in the system for leak testing.  When nitrogen is used to boost system pressure for testing, ensure that it is eliminated from the system before charging. Minimum refrigerant leak field test pressure shall be as specified in ANSI/ASHRAE 15 & 34, except that test pressure shall not exceed 150 psig on hermetic compressors unless otherwise specified as a low side test pressure on the equipment nameplate.  If leaks are detected at time of installation or during warranty period, remove the entire refrigerant charge from the system, correct leaks, and retest system.

### 3.6.2   Evacuation, Dehydration, and Charging

After field charged refrigerant system is found to be without leaks or after leaks have been repaired on field-charged and factory-charged systems, evacuate the system using a reliable gage and a vacuum pump capable of pulling a vacuum of at least one mm Hg absolute.  Evacuate system in accordance with the triple-evacuation and blotter method or in accordance with equipment manufacturer's printed instructions and recharge system.

### 3.6.3   Start-Up and Initial Operational Tests

Test the air conditioning systems and systems components for proper operation.  Adjust safety and automatic control instruments as necessary to ensure proper operation and sequence.  Conduct operational tests for not less than 8 hours.

### 3.6.4   Performance Tests

Upon completion of evacuation, charging, startup, final leak testing, and proper adjustment of controls, test the systems to demonstrate compliance with performance and capacity requirements.  Test systems for not less than 8 hours, record readings hourly.  At the end of the test period, average the readings and the average shall be considered to be the system performance.

-- End of Section --

SECTION 26 00 00

BASIC ELECTRICAL MATERIALS AND METHODS

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

ASTM INTERNATIONAL (ASTM)

ASTM D709	(2017) Standard Specification for Laminated Thermosetting Materials

INSTITUTE OF ELECTRICAL AND ELECTRONICS ENGINEERS (IEEE)

IEEE 100	(2000; Archived) The Authoritative Dictionary of IEEE Standards Terms

IEEE C2	(2017; Errata 1-2 2017; INT 1 2017) National Electrical Safety Code

IEEE C57.12.28	(2014) Standard for Pad-Mounted Equipment - Enclosure Integrity

IEEE C57.12.29	(2014) Standard for Pad-Mounted Equipment - Enclosure Integrity for Coastal Environments

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

NEMA 250	(2014) Enclosures for Electrical Equipment (1000 Volts Maximum)

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 70	(2017; ERTA 1-2 2017; TIA 17-1; TIA 17-2; TIA 17-3) National Electrical Code

## 1.2   RELATED REQUIREMENTS

This section applies to all sections of Division 26, ELECTRICAL of this project specification unless specified otherwise in the individual sections.  This section has been incorporated into, and thus, does not apply to, and is not referenced in the following sections.

Section 26 20 00 INTERIOR DISTRIBUTION SYSTEM

## 1.3   DEFINITIONS

a.  Unless otherwise specified or indicated, electrical and electronics terms used in these specifications, and on the drawings, shall be as defined in IEEE 100.

b.  The technical sections referred to herein are those specification sections that describe products, installation procedures, and equipment operations and that refer to this section for detailed description of submittal types.

c.  The technical paragraphs referred to herein are those paragraphs in PART 2 - PRODUCTS and PART 3 - EXECUTION of the technical sections that describe products, systems, installation procedures, equipment, and test methods.

## 1.4   ADDITIONAL SUBMITTALS INFORMATION

Submittals required in other sections that refer to this section must conform to the following additional requirements as applicable.

### 1.4.1   Shop Drawings (SD-02)

Include wiring diagrams and installation details of equipment indicating proposed location, layout and arrangement, control panels, accessories, piping, ductwork, and other items that must be shown to ensure a coordinated installation.  Wiring diagrams shall identify circuit terminals and indicate the internal wiring for each item of equipment and the interconnection between each item of equipment.  Drawings shall indicate adequate clearance for operation, maintenance, and replacement of operating equipment devices.

### 1.4.2   Product Data (SD-03)

Submittal shall include performance and characteristic curves.

## 1.5   QUALITY ASSURANCE

### 1.5.1   Regulatory Requirements

In each of the publications referred to herein, consider the advisory provisions to be mandatory, as though the word, "shall" had been substituted for "should" wherever it appears.  Interpret references in these publications to the "authority having jurisdiction," or words of similar meaning, to mean the Contracting Officer.  Equipment, materials, installation, and workmanship shall be in accordance with the mandatory and advisory provisions of NFPA 70 unless more stringent requirements are specified or indicated.

### 1.5.2   Standard Products

Provide materials and equipment that are products of manufacturers regularly engaged in the production of such products which are of equal material, design and workmanship.  Products shall have been in satisfactory commercial or industrial use for 2 years prior to bid opening.  The 2-year period shall include applications of equipment and materials under similar circumstances and of similar size.  The product shall have been on sale on the commercial market through advertisements, manufacturers' catalogs, or brochures during the 2-year period.  Where two or more items of the same class of equipment are required, these items shall be products of a single manufacturer; however, the component parts of the item need not be the products of the same manufacturer unless stated in the technical section.

#### 1.5.2.1   Alternative Qualifications

Products having less than a 2-year field service record will be acceptable if a certified record of satisfactory field operation for not less than 6000 hours, exclusive of the manufacturers' factory or laboratory tests, is furnished.

#### 1.5.2.2   Material and Equipment Manufacturing Date

Products manufactured more than 3 years prior to date of delivery to site shall not be used, unless specified otherwise.

## 1.6   WARRANTY

The equipment items shall be supported by service organizations which are reasonably convenient to the equipment installation in order to render satisfactory service to the equipment on a regular and emergency basis during the warranty period of the contract.

## 1.7   POSTED OPERATING INSTRUCTIONS

Provide for each system and principal item of equipment as specified in the technical sections for use by operation and maintenance personnel.  The operating instructions shall include the following:

a.  Wiring diagrams, control diagrams, and control sequence for each principal system and item of equipment.

b.  Start up, proper adjustment, operating, lubrication, and shutdown procedures.

c.  Safety precautions.

d.  The procedure in the event of equipment failure.

e.  Other items of instruction as recommended by the manufacturer of each system or item of equipment.

Print or engrave operating instructions and frame under glass or in approved laminated plastic.  Post instructions where directed.  For operating instructions exposed to the weather, provide weather-resistant materials or weatherproof enclosures.  Operating instructions shall not fade when exposed to sunlight and shall be secured to prevent easy removal or peeling.

## 1.8   MANUFACTURER'S NAMEPLATE

Each item of equipment shall have a nameplate bearing the manufacturer's name, address, model number, and serial number securely affixed in a conspicuous place; the nameplate of the distributing agent will not be acceptable.

## 1.9   FIELD FABRICATED NAMEPLATES

ASTM D709.  Provide laminated plastic nameplates for each equipment enclosure, relay, switch, and device; as specified in the technical sections or as indicated on the drawings.  Each nameplate inscription shall identify the function and, when applicable, the position.  Nameplates shall be melamine plastic, 0.125 inch thick, white with black center core.  Surface shall be matte finish.  Corners shall be square.  Accurately align lettering and engrave into the core.  Minimum size of nameplates shall be one by 2.5 inches.  Lettering shall be a minimum of 0.25 inch high normal block style.

## 1.10   WARNING SIGNS

Provide warning signs for the enclosures of electrical equipment including substations, pad-mounted transformers, pad-mounted switches, generators, and switchgear having a nominal rating exceeding 600 volts.

a.  When the enclosure integrity of such equipment is specified to be in accordance with IEEE C57.12.28 or IEEE C57.12.29, such as for pad-mounted transformers, provide self-adhesive warning signs on the outside of the high voltage compartment door(s).  Sign shall be a decal and shall have nominal dimensions of 7 by 10 inches with the legend "DANGER HIGH VOLTAGE" printed in two lines of nominal 2 inch high letters.  The word "DANGER" shall be in white letters on a red background and the words "HIGH VOLTAGE" shall be in black letters on a white background.  Decal shall be Panduit No. PPSO710D72 or approved equal.

## 1.11   ELECTRICAL REQUIREMENTS

Electrical installations shall conform to IEEE C2, NFPA 70, and requirements specified herein.

## 1.12   INSTRUCTION TO GOVERNMENT PERSONNEL

Where specified in the technical sections, furnish the services of competent instructors to give full instruction to designated Government personnel in the adjustment, operation, and maintenance of the specified systems and equipment, including pertinent safety requirements as required. Instructors shall be thoroughly familiar with all parts of the installation and shall be trained in operating theory as well as practical operation and maintenance work.  Instruction shall be given during the first regular work week after the equipment or system has been accepted and turned over to the Government for regular operation.  The number of man-days (8 hours per day) of instruction furnished shall be as specified in the individual section.

# PART 2   PRODUCTS

## 2.1   FACTORY APPLIED FINISH

Electrical equipment shall have factory-applied painting systems which shall, as a minimum, meet the requirements of NEMA 250 corrosion-resistance test.

# PART 3   EXECUTION

## 3.1   FIELD APPLIED PAINTING

Paint electrical equipment as required to match finish of adjacent surfaces or to meet the indicated or specified safety criteria.

## 3.2   FIELD FABRICATED NAMEPLATE MOUNTING

Provide number, location, and letter designation of nameplates as indicated.  Fasten nameplates to the device with a minimum of two sheet-metal screws or two rivets.

## 3.3   WARNING SIGN MOUNTING

Provide the number of signs required to be readable from each accessible side, but space the signs a maximum of 30 feet apart.

-- End of Section --

SECTION 26 20 00

INTERIOR DISTRIBUTION SYSTEM

# PART 1   GENERAL

## 1.1   REFERENCES

The publications listed below form a part of this specification to the extent referenced.  The publications are referred to in the text by the basic designation only.

ASTM INTERNATIONAL (ASTM)

ASTM B1	(2013) Standard Specification for Hard-Drawn Copper Wire

ASTM B8	(2011; R 2017) Standard Specification for Concentric-Lay-Stranded Copper Conductors, Hard, Medium-Hard, or Soft

ASTM D709	(2017) Standard Specification for Laminated Thermosetting Materials

INSTITUTE OF ELECTRICAL AND ELECTRONICS ENGINEERS (IEEE)

IEEE 100	(2000; Archived) The Authoritative Dictionary of IEEE Standards Terms

IEEE 81	(2012) Guide for Measuring Earth Resistivity, Ground Impedance, and Earth Surface Potentials of a Ground System

IEEE C2	(2017; Errata 1-2 2017; INT 1 2017) National Electrical Safety Code

NATIONAL ELECTRICAL MANUFACTURERS ASSOCIATION (NEMA)

ANSI C80.1	(2005) American National Standard for Electrical Rigid Steel Conduit (ERSC)

ANSI C80.3	(2015) American National Standard for Electrical Metallic Tubing (EMT)

ANSI C80.5	(2015) American National Standard for Electrical Rigid Aluminum Conduit

NEMA 250	(2014) Enclosures for Electrical Equipment (1000 Volts Maximum)

NEMA ICS 1	(2000; R 2015) Standard for Industrial Control and Systems: General Requirements

NEMA ICS 6	(1993; R 2016) Industrial Control and Systems:  Enclosures

NEMA KS 1	(2013) Enclosed and Miscellaneous Distribution Equipment Switches (600 V Maximum)

NEMA RN 1	(2005; R 2013) Polyvinyl-Chloride (PVC) Externally Coated Galvanized Rigid Steel Conduit and Intermediate Metal Conduit

NEMA TC 2	(2013) Standard for Electrical Polyvinyl Chloride (PVC) Conduit

NEMA TC 3	(2016) Polyvinyl Chloride (PVC) Fittings for Use With Rigid PVC Conduit and Tubing

NEMA WD 1	(1999; R 2015) Standard for General Color Requirements for Wiring Devices

NEMA WD 6	(2016) Wiring Devices Dimensions Specifications

NEMA Z535.4	(2011) American National Standard for Product Safety Signs and Labels

NATIONAL FIRE PROTECTION ASSOCIATION (NFPA)

NFPA 70	(2017; ERTA 1-2 2017; TIA 17-1; TIA 17-2; TIA 17-3) National Electrical Code

NFPA 70E	(2015; ERTA 1 2015) Standard for Electrical Safety in the Workplace

TELECOMMUNICATIONS INDUSTRY ASSOCIATION (TIA)

TIA-607	(2011b) Generic Telecommunications Bonding and Grounding (Earthing) for Customer Premises

UNDERWRITERS LABORATORIES (UL)

UL 1	(2005; Reprint Aug 2017) UL Standard for Safety Flexible Metal Conduit

UL 1449	(2014; Reprint Jul 2017) UL Standard for Safety Surge Protective Devices

UL 1660	(2014) Liquid-Tight Flexible Nonmetallic Conduit

UL 20	(2010; Reprint Feb 2012) General-Use Snap Switches

UL 360	(2013; Reprint Jan 2015) Liquid-Tight Flexible Steel Conduit

UL 467	(2013; Reprint Jun 2017) UL Standard for Safety Grounding and Bonding Equipment

UL 486A-486B	(2013; Reprint Jan 2016) Wire Connectors

UL 486C	(2013; Reprint Jan 2016) Splicing Wire Connectors

UL 489	(2016) UL Standard for Safety Molded-Case Circuit Breakers, Molded-Case Switches and Circuit-Breaker Enclosures

UL 498	(2017; Reprint Jul 2017) UL Standard for Safety Attachment Plugs and Receptacles

UL 50	(2015) UL Standard for Safety Enclosures for Electrical Equipment, Non-Environmental Considerations

UL 510	(2017) UL Standard for Safety Polyvinyl Chloride, Polyethylene and Rubber Insulating Tape

UL 514A	(2013; Reprint Aug 2017) UL Standard for Safety Metallic Outlet Boxes

UL 514B	(2012; Reprint Nov 2014) Conduit, Tubing and Cable Fittings

UL 514C	(2014; Reprint Dec 2014) Nonmetallic Outlet Boxes, Flush-Device Boxes, and Covers

UL 6	(2007; Reprint Nov 2014) Electrical Rigid Metal Conduit-Steel

UL 651	(2011; Reprint Jun 2016) UL Standard for Safety Schedule 40 and 80 Rigid PVC Conduit and Fittings

UL 67	(2009; Reprint Dec 2016) UL Standard for Safety Panelboards

UL 6A	(2008; Reprint Nov 2014) Electrical Rigid Metal Conduit - Aluminum, Red Brass, and Stainless Steel

UL 797	(2007; Reprint Mar 2017) UL Standard for Safety Electrical Metallic Tubing -- Steel

UL 83	(2017) UL Standard for Safety Thermoplastic-Insulated Wires and Cables

UL 869A	(2006) Reference Standard for Service Equipment

UL 870	(2016) UL Standard for Safety Wireways, Auxiliary Gutters, and Associated Fittings

UL 943	(2016) UL Standard for Safety Ground-Fault Circuit-Interrupters

## 1.2   DEFINITIONS

Unless otherwise specified or indicated, electrical and electronics terms used in these specifications, and on the drawings, are as defined in IEEE 100.

## 1.3   SUBMITTALS

Contracting Officer’s written approval is required for submittals. Submit the following in accordance with Section 01 33 00 SUBMITTAL PROCEDURES:

SD-03 Product Data

Receptacles

Circuit breakers

Switches

Enclosed circuit breakers

Surge protective devices

Include performance and characteristic curves.

SD-06 Test Reports

600-volt wiring test

Grounding system test

Ground-fault receptacle test

## 1.4   QUALITY ASSURANCE

### 1.4.1   Regulatory Requirements

In each of the publications referred to herein, consider the advisory provisions to be mandatory, as though the word, "shall" or "must" had been substituted for "should" wherever it appears.  Interpret references in these publications to the "authority having jurisdiction," or words of similar meaning, to mean the Contracting Officer.  Provide equipment, materials, installation, and workmanship in accordance with the mandatory and advisory provisions of NFPA 70 unless more stringent requirements are specified or indicated.

### 1.4.2   Standard Products

Provide materials and equipment that are products of manufacturers regularly engaged in the production of such products which are of equal material, design and workmanship and:

a.  Have been in satisfactory commercial or industrial use for 2 years prior to bid opening including applications of equipment and materials under similar circumstances and of similar size.

b.  Have been on sale on the commercial market through advertisements, manufacturers' catalogs, or brochures during the 2-year period.

c.  Where two or more items of the same class of equipment are required, provide products of a single manufacturer; however, the component parts of the item need not be the products of the same manufacturer unless stated in this section.

#### 1.4.2.1   Alternative Qualifications

Products having less than a 2-year field service record will be acceptable if a certified record of satisfactory field operation for not less than 6000 hours, exclusive of the manufacturers' factory or laboratory tests, is furnished.

#### 1.4.2.2   Material and Equipment Manufacturing Date

Products manufactured more than 3 years prior to date of delivery to site are not acceptable.

## 1.5   WARRANTY

Provide equipment items supported by service organizations that are reasonably convenient to the equipment installation in order to render satisfactory service to the equipment on a regular and emergency basis during the warranty period of the contract.

# PART 2   PRODUCTS

## 2.1   MATERIALS AND EQUIPMENT

As a minimum, meet requirements of UL, where UL standards are established for those items, and requirements of NFPA 70 for all materials, equipment, and devices.

## 2.2   CONDUIT AND FITTINGS

Conform to the following:

### 2.2.1   Rigid Metallic Conduit

#### 2.2.1.1   Rigid, Threaded Zinc-Coated Steel Conduit

ANSI C80.1, UL 6.

#### 2.2.1.2   Rigid Aluminum Conduit

ANSI C80.5, UL 6A.

### 2.2.2   Rigid Nonmetallic Conduit

PVC Type EPC-40 in accordance with NEMA TC 2, UL 651.

### 2.2.3   Electrical, Zinc-Coated Steel Metallic Tubing (EMT)

UL 797, ANSI C80.3.

### 2.2.4   Plastic-Coated Rigid Steel and IMC Conduit

NEMA RN 1, Type 40 (40 mils thick).

### 2.2.5   Flexible Metal Conduit

UL 1.

#### 2.2.5.1   Liquid-Tight Flexible Metal Conduit, Steel

UL 360.

### 2.2.6   Fittings for Metal Conduit, EMT, and Flexible Metal Conduit

UL 514B.  Ferrous fittings:  cadmium- or zinc-coated in accordance with UL 514B.

#### 2.2.6.1   Fittings for Rigid Metal Conduit and IMC

Threaded-type.  Split couplings unacceptable.

#### 2.2.6.2   Fittings for EMT

Steel compression type.

### 2.2.7   Fittings for Rigid Nonmetallic Conduit

NEMA TC 3 for PVC, and UL 514B.

### 2.2.8   Liquid-Tight Flexible Nonmetallic Conduit

UL 1660.

## 2.3   OUTLET BOXES AND COVERS

UL 514A, cadmium- or zinc-coated, if ferrous metal.  UL 514C, if nonmetallic.

## 2.4   CABINETS, JUNCTION BOXES, AND PULL BOXES

Volume greater than 100 cubic inches, UL 50, hot-dip, zinc-coated, if sheet steel.

## 2.5   WIRES AND CABLES

Provide wires and cables in accordance applicable requirements of NFPA 70 and UL for type of insulation, jacket, and conductor specified or indicated.  Do not use wires and cables manufactured more than 12 months prior to date of delivery to site.

### 2.5.1   Conductors

Provide the following:

a.  Conductor sizes and capacities shown are based on copper, unless indicated otherwise.

b.  Conductors No. 8 AWG and larger diameter:  stranded.

c.  Conductors No. 10 AWG and smaller diameter:  solid.

d.  Conductors for remote control, alarm, and signal circuits, classes 1, 2, and 3:  stranded unless specifically indicated otherwise.

e.  All conductors:  copper.

#### 2.5.1.1   Minimum Conductor Sizes

Provide minimum conductor size in accordance with the following:

a.  Branch circuits:  No. 12 AWG.

b.  Class 1 remote-control and signal circuits:  No. 14 AWG.

c.  Class 2 low-energy, remote-control and signal circuits:  No. 16 AWG.

d.  Class 3 low-energy, remote-control, alarm and signal circuits:  No. 22 AWG.

### 2.5.2   Color Coding

Provide color coding for service, feeder, branch, control, and signaling circuit conductors.

#### 2.5.2.1   Ground and Neutral Conductors

Provide color coding of ground and neutral conductors as follows:

a.  Grounding conductors:  Green.

b.  Neutral conductors:  White.

c.  Exception, where neutrals of more than one system are installed in same raceway or box, other neutrals color coding:  white with a different colored (not green) stripe for each.

#### 2.5.2.2   Ungrounded Conductors

Provide color coding of ungrounded conductors in different voltage systems as follows:

a.  208/120 volt, three-phase

(1)  Phase A - black

(2)  Phase B - red

(3)  Phase C - blue

### 2.5.3   Insulation

Unless specified or indicated otherwise or required by NFPA 70, provide power and lighting wires rated for 600-volts, Type THWN/THHN conforming to UL 83, except that grounding wire may be type TW conforming to UL 83; remote-control and signal circuits:  Type TW or TF, conforming to UL 83.  Where lighting fixtures require 90-degree Centigrade (C) conductors, provide only conductors with 90-degree C insulation or better.

### 2.5.4   Bonding Conductors

ASTM B1, solid bare copper wire for sizes No. 8 AWG and smaller diameter; ASTM B8, Class B, stranded bare copper wire for sizes No. 6 AWG and larger diameter.

## 2.6   SPLICES AND TERMINATION COMPONENTS

UL 486A-486B for wire connectors and UL 510 for insulating tapes.  Connectors for No. 10 AWG and smaller diameter wires:  insulated, pressure-type in accordance with UL 486A-486B or UL 486C (twist-on splicing connector).  Provide solderless terminal lugs on stranded conductors.

## 2.7   DEVICE PLATES

Provide the following:

a.  UL listed, one-piece device plates for outlets to suit the devices installed.

b.  For metal outlet boxes, plates on unfinished walls:  zinc-coated sheet steel or cast metal having round or beveled edges.

c.  For nonmetallic boxes and fittings, other suitable plates may be provided.

d.  Plates on finished walls:  satin finish stainless steel or brushed-finish aluminum, minimum 0.03 inch thick.

e.  Screws:  machine-type with countersunk heads in color to match finish of plate.

f.  Sectional type device plates are not be permitted.

g.  Plates installed in wet locations:  gasketed and UL listed for "wet locations."

## 2.8   SWITCHES

### 2.8.1   Toggle Switches

NEMA WD 1, UL 20, single pole, double pole, three-way, and four-way, totally enclosed with bodies of thermoplastic or thermoset plastic and mounting strap with grounding screw.  Include the following:

a.  Handles:  brown thermoplastic.

b.  Wiring terminals:  screw-type, side-wired.

c.  Contacts:  silver-cadmium and contact arm - one-piece copper alloy.

d.  Switches:  rated quiet-type ac only, 120/277 volts, with current rating and number of poles indicated.

### 2.8.2   Disconnect Switches

NEMA KS 1.  Provide heavy duty-type switches where indicated, where switches are rated higher than 240 volts, and for double-throw switches.  Utilize Class R fuseholders and fuses for fused switches, unless indicated otherwise.  Provide horsepower rated for switches serving as the motor-disconnect means.  Provide switches in NEMA 1 or 3R, enclosure as indicated per NEMA ICS 6.

## 2.9   RECEPTACLES

Provide the following:

a.  UL 498, hard use (also designated heavy-duty), grounding-type.

b.  Ratings and configurations:  as indicated.

c.  Bodies:  brown as per NEMA WD 1.

d.  Face and body:  thermoplastic supported on a metal mounting strap.

e.  Dimensional requirements:  per NEMA WD 6.

f.  Screw-type, side-wired wiring terminals or of the solderless pressure type having suitable conductor-release arrangement.

g.  Grounding pole connected to mounting strap.

h.  The receptacle:  containing triple-wipe power contacts and double or triple-wipe ground contacts.

### 2.9.1   Switched Duplex Receptacles

Provide separate terminals for each ungrounded pole.  Top receptacle:  switched when installed.

### 2.9.2   Weatherproof Receptacles

Provide receptacles, UL listed for use in "wet locations".  Include cast metal box with gasketed, hinged, lockable and weatherproof while-in-use, polycarbonate, UV resistant/stabilized cover plate.

### 2.9.3   Ground-Fault Circuit Interrupter Receptacles (GFI)

UL 943, duplex type for mounting in standard outlet box.  Provide device capable of detecting current leak of 6 milliamperes or greater and tripping per requirements of UL 943 for Class A ground-fault circuit interrupter devices.  Provide screw-type, side-wired wiring terminals or pre-wired (pigtail) leads.

## 2.10   PANELBOARDS

Provide panelboards in accordance with the following:

a.  UL 67 and UL 50 having a short-circuit current rating as indicated.

b.  Panelboards for use as service disconnecting means:  additionally conform to UL 869A.

c.  Panelboards:  circuit breaker-equipped.

d.  Designed such that individual breakers can be removed without disturbing adjacent units or without loosening or removing supplemental insulation supplied as means of obtaining clearances as required by UL.

e.  "Specific breaker placement" is required in panelboards to match the breaker placement indicated in the panelboard schedule on the drawings.

f.  Use of "Subfeed Breakers" is not acceptable unless specifically indicated otherwise.

g.  Main breaker:  "separately" mounted branch breakers.

h.  Where "space only" is indicated, make provisions for future installation of breakers.

i.  Directories:  indicate load served by each circuit in panelboard.

j.  Directories:  indicate source of service to panelboard (e.g., Panel PA served from Panel MDP).

k.  Provide new directories for existing panels modified by this project as indicated.

l.  Type directories and mount in holder behind transparent protective covering.

m.  Panelboards:  listed and labeled for their intended use.

n.  Panelboard nameplates:  provided in accordance with paragraph FIELD FABRICATED NAMEPLATES.

### 2.10.1   Enclosure

Provide panelboard enclosure in accordance with the following:

a.  UL 50.

b.  Cabinets mounted outdoors or flush-mounted:  hot-dipped galvanized after fabrication.

c.  Cabinets:  painted in accordance with paragraph PAINTING.

d.  Outdoor cabinets:  NEMA 3R raintight with conduit hubs welded to the cabinet.

e.  Front edges of cabinets:  form-flanged or fitted with structural shapes welded or riveted to the sheet steel, for supporting the panelboard front.

f.  All cabinets:  fabricated such that no part of any surface on the finished cabinet deviates from a true plane by more than 1/8 inch.

g.  Holes:  provided in the back of indoor surface-mounted cabinets, with outside spacers and inside stiffeners, for mounting the cabinets with a 1/2 inch clear space between the back of the cabinet and the wall surface.

h.  Flush doors:  mounted on hinges that expose only the hinge roll to view when the door is closed.

i.  Each door:  fitted with a combined catch and lock, except that doors over 24 inches long provided with a three-point latch having a knob with a T-handle, and a cylinder lock.

j.  Keys:  two provided with each lock, with all locks keyed alike.

k.  Finished-head cap screws:  provided for mounting the panelboard fronts on the cabinets.

### 2.10.2   Panelboard Buses

Support bus bars on bases independent of circuit breakers.  Design main buses and back pans so that breakers may be changed without machining, drilling, or tapping.  Provide isolated neutral bus in each panel for connection of circuit neutral conductors.  Provide separate ground bus identified as equipment grounding bus per UL 67 for connecting grounding conductors; bond to steel cabinet.

### 2.10.3   Circuit Breakers

UL 489, thermal magnetic-type having a minimum short-circuit current rating equal to the short-circuit current rating of the panelboard in which the circuit breaker will be mounted.  Breaker terminals:  UL listed as suitable for type of conductor provided.  Where indicated on the drawings, provide circuit breakers with shunt trip devices.  Series rated circuit breakers and plug-in circuit breakers are unacceptable.

#### 2.10.3.1   Multipole Breakers

Provide common trip-type with single operating handle.  Design breaker such that overload in one pole automatically causes all poles to open.  Maintain phase sequence throughout each panel so that any three adjacent breaker poles are connected to Phases A, B, and C, respectively.

#### 2.10.3.2   Circuit Breaker With Ground-Fault Circuit Interrupter

UL 943 and NFPA 70.  Provide with "push-to-test" button, visible indication of tripped condition, and ability to detect and trip on current imbalance of 6 milliamperes or greater per requirements of UL 943 for Class A ground-fault circuit interrupter.

#### 2.10.3.3   Circuit Breakers for HVAC Equipment

Provide circuit breakers for HVAC equipment having motors (group or individual) marked for use with HACR type and UL listed as HACR type.

## 2.11   ENCLOSED CIRCUIT BREAKERS

UL 489.  Individual molded case circuit breakers with voltage and continuous current ratings, number of poles, overload trip setting, and short circuit current interrupting rating as indicated.  Enclosure type as indicated.  Provide solid neutral.

## 2.12   GROUNDING AND BONDING EQUIPMENT

### 2.12.1   Ground Rods

UL 467.  Ground rods:   copper-clad steel, with minimum diameter of 3/4 inch and minimum length 10 feet.  Sectional ground rods are permitted.

### 2.12.2   Ground Bus

Copper ground bus:  provided in the electrical equipment rooms as indicated.

## 2.13   MANUFACTURER'S NAMEPLATE

Provide on each item of equipment a nameplate bearing the manufacturer's name, address, model number, and serial number securely affixed in a conspicuous place; the nameplate of the distributing agent will not be acceptable.

## 2.14   FIELD FABRICATED NAMEPLATES

Provide field fabricated nameplates in accordance with the following:

a.  ASTM D709.

b.  Provide laminated plastic nameplates for each equipment enclosure, relay, switch, and device; as specified or as indicated on the drawings.

c.  Each nameplate inscription:  identify the function and, when applicable, the position.

d.  Nameplates:  melamine plastic, 0.125 inch thick, white with black center core.

e.  Surface:  matte finish.  Corners:  square.  Accurately align lettering and engrave into the core.

f.  Minimum size of nameplates:   one by 2.5 inches.

g.  Lettering size and style:  a minimum of 0.25 inch high normal block style.

## 2.15   WARNING SIGNS

Provide warning signs for flash protection in accordance with NFPA 70E and NEMA Z535.4 for switchboards, panelboards, industrial control panels, and motor control centers that are in other than dwelling occupancies and are likely to require examination, adjustment, servicing, or maintenance while energized.  Provide field installed signs to warn qualified persons of potential electric arc flash hazards when warning signs are not provided by the manufacturer.  Provide marking that is clearly visible to qualified persons before examination, adjustment, servicing, or maintenance of the equipment.

## 2.16   FIRESTOPPING MATERIALS

Provide firestopping around electrical penetrations to maintain wall rating.

## 2.17   WIREWAYS

UL 870.  Material:  steel epoxy painted 16 gauge for heights and depths up to 6 by 6 inches, and 14 gauge for heights and depths up to 12 by 12 inches.  Provide in length required for the application with screw- cover NEMA 1 or 3R enclosure per NEMA ICS 6.

## 2.18   SURGE PROTECTIVE DEVICES

Provide parallel type surge protective devices (SPD) which comply with UL 1449 at the service entrance panelboards.  Provide surge protectors in a NEMA 1 enclosure per NEMA ICS 6.  Use Type 1 or Type 2 SPD and connect on the load side of a dedicated circuit breaker.

Provide the following modes of protection:

FOR SINGLE PHASE AND THREE PHASE WYE CONNECTED SYSTEMS-

Phase to phase ( L-L )

Each phase to neutral ( L-N )

Neutral to ground ( N-G )

Phase to ground ( L-G )

SPDs at the service entrance:  provide with a minimum surge current rating of 80,000 amperes for L-L mode minimum and 40,000 amperes for other modes (L-N, L-G, and N-G) and downstream SPDs rated 40,000 amperes for L-L mode minimum and 20,000 amperes for other modes (L-N, L-G, and N-G).

The minimum MCOV (Maximum Continuous Operating Voltage) rating for L-N and L-G modes of operation:  120% of nominal voltage for 240 volts and below; 115% of nominal voltage above 240 volts to 480 volts.

## 2.19   FACTORY APPLIED FINISH

Provide factory-applied finish on electrical equipment in accordance with the following:

a.  NEMA 250 corrosion-resistance test and the additional requirements as specified herein.

b.  Interior and exterior steel surfaces of equipment enclosures:  thoroughly cleaned followed by a rust-inhibitive phosphatizing or equivalent treatment prior to painting.

c.  Exterior surfaces:  free from holes, seams, dents, weld marks, loose scale or other imperfections.

d.  Interior surfaces:  receive not less than one coat of corrosion-resisting paint in accordance with the manufacturer's standard practice.

e.  Exterior surfaces:  primed, filled where necessary, and given not less than two coats baked enamel with semigloss finish.

f.  Equipment located indoors:  ANSI Light Gray, and equipment located outdoors:  ANSI Light Gray.

g.  Provide manufacturer's coatings for touch-up work and as specified in paragraph FIELD APPLIED PAINTING.

# PART 3   EXECUTION

## 3.1   INSTALLATION

Electrical installations, including weatherproof and hazardous locations and ducts, plenums and other air-handling spaces:  conform to requirements of NFPA 70 and IEEE C2 and to requirements specified herein.

### 3.1.1   Wiring Methods

Provide insulated conductors installed in rigid steel conduit, IMC, rigid nonmetallic conduit, or EMT, except where specifically indicated or specified otherwise or required by NFPA 70 to be installed otherwise.  Grounding conductor:  separate from electrical system neutral conductor.  Provide insulated green equipment grounding conductor for circuit(s) installed in conduit and raceways.  Shared neutral, or multi-wire branch circuits, are not permitted with arc-fault circuit interrupters.  Minimum conduit size:   1/2 inch in diameter for low voltage lighting and power circuits.  Vertical distribution in multiple story buildings:  made with metal conduit in fire-rated shafts, with metal conduit extending through shafts for minimum distance of 6 inches.

#### 3.1.1.1   Pull Wire

Install pull wires in empty conduits.  Pull wire:  plastic having minimum 200-pound force tensile strength.  Leave minimum 36 inches of slack at each end of pull wire.

### 3.1.2   Conduit Installation

Unless indicated otherwise, conceal conduit under floor slabs and within finished walls, ceilings, and floors.  Keep conduit minimum 6 inches away from parallel runs of flues and steam or hot water pipes.  Install conduit parallel with or at right angles to ceilings, walls, and structural members where located above accessible ceilings and where conduit will be visible after completion of project.  Run conduits in crawl space as if exposed.

#### 3.1.2.1   Restrictions Applicable to Aluminum Conduit

a.  Do not install underground or encase in concrete or masonry.

b.  Do not use brass or bronze fittings.

c.  Do not use when the enclosed conductors must be shielded from the effects of High-altitude Electromagnetic Pulse (HEMP).

#### 3.1.2.2   Restrictions Applicable to EMT

a.  Do not install underground.

b.  Do not encase in concrete, mortar, grout, or other cementitious materials.

c.  Do not use in areas subject to severe physical damage including but not limited to equipment rooms where moving or replacing equipment could physically damage the EMT.

d.  Do not use in hazardous areas.

e.  Do not use outdoors.

f.  Do not use in fire pump rooms.

g.  Do not use when the enclosed conductors must be shielded from the effects of High-altitude Electromagnetic Pulse (HEMP).

#### 3.1.2.3   Restrictions Applicable to Nonmetallic Conduit

a.  PVC Schedule 40 and PVC Schedule 80

(1)  Do not use in areas where subject to severe physical damage, including but not limited to, mechanical equipment rooms, electrical equipment rooms, hospitals, power plants, missile magazines, and other such areas.

(2)  Do not use in hazardous (classified) areas.

(3)  Do not use in fire pump rooms.

(4)  Do not use in penetrating fire-rated walls or partitions, or fire-rated floors.

(5)  Do not use above grade, except where allowed in this section for rising through floor slab or indicated otherwise.

(6)  Do not use when the enclosed conductors must be shielded from the effects of High-altitude Electromagnetic Pulse (HEMP).

#### 3.1.2.4   Restrictions Applicable to Flexible Conduit

Use only as specified in paragraph FLEXIBLE CONNECTIONS.  Do not use when the enclosed conductors must be shielded from the effects of High-altitude Electromagnetic Pulse (HEMP).

#### 3.1.2.5   Underground Conduit

Plastic-coated rigid steel; plastic-coated steel IMC; PVC, Type EPC-40.  Convert nonmetallic conduit, other than PVC Schedule 40 or 80, to plastic-coated rigid, or IMC, steel conduit before rising through floor slab.  Plastic coating:  extend minimum 6 inches above floor.

#### 3.1.2.6   Stub-Ups

Provide conduits stubbed up through concrete floor for connection to free-standing equipment with adjustable top or coupling threaded inside for plugs, set flush with finished floor.  Extend conductors to equipment in rigid steel conduit, except that flexible metal conduit may be used 6 inches above floor.  Where no equipment connections are made, install screwdriver-operated threaded flush plugs in conduit end.

#### 3.1.2.7   Conduit Support

Support conduit by pipe straps, wall brackets, threaded rod conduit hangers, or ceiling trapeze. Fasten by wood screws to wood; by toggle bolts on hollow masonry units; by concrete inserts or expansion bolts on concrete or brick; and by machine screws, welded threaded studs, or spring-tension clamps on steel work. Threaded C-clamps may be used on rigid steel conduit only.  Do not weld conduits or pipe straps to steel structures.  Do not exceed one-fourth proof test load for load applied to fasteners.  Provide vibration resistant and shock-resistant fasteners attached to concrete ceiling.  Do not cut main reinforcing bars for any holes cut to depth of more than 1 1/2 inches in reinforced concrete beams or to depth of more than 3/4 inch in concrete joints.  Fill unused holes.  In partitions of light steel construction, use sheet metal screws.  In suspended-ceiling construction, run conduit above ceiling.  Do not support conduit by ceiling support system.  Conduit and box systems:  supported independently of both (a) tie wires supporting ceiling grid system, and (b) ceiling grid system into which ceiling panels are placed.  Do not share supporting means between electrical raceways and mechanical piping or ducts.  Coordinate installation with above-ceiling mechanical systems to assure maximum accessibility to all systems.  Spring-steel fasteners may be used for lighting branch circuit conduit supports in suspended ceilings in dry locations.   Support exposed risers in wire shafts of multistory buildings by U-clamp hangers at each floor level and at 10 foot maximum intervals. Where conduit crosses building expansion joints, provide suitable watertight expansion fitting that maintains conduit electrical continuity by bonding jumpers or other means.  For conduits greater than 2 1/2 inches inside diameter, provide supports to resist forces of 0.5 times the equipment weight in any direction and 1.5 times the equipment weight in the downward direction.

#### 3.1.2.8   Directional Changes in Conduit Runs

Make changes in direction of runs with symmetrical bends or cast-metal fittings.  Make field-made bends and offsets with hickey or conduit-bending machine.  Do not install crushed or deformed conduits.  Avoid trapped conduits.  Prevent plaster, dirt, or trash from lodging in conduits, boxes, fittings, and equipment during construction.  Free clogged conduits of obstructions.

#### 3.1.2.9   Locknuts and Bushings

Fasten conduits to sheet metal boxes and cabinets with two locknuts where required by NFPA 70, where insulated bushings are used, and where bushings cannot be brought into firm contact with the box; otherwise, use at least minimum single locknut and bushing.  Provide locknuts with sharp edges for digging into wall of metal enclosures.  Install bushings on ends of conduits, and provide insulating type where required by NFPA 70.

#### 3.1.2.10   Flexible Connections

Provide flexible steel conduit between 3 and 6 feet in length for recessed and semirecessed lighting fixtures; for equipment subject to vibration, noise transmission, or movement; and for motors.  Install flexible conduit to allow 20 percent slack.  Minimum flexible steel conduit size:   1/2 inch diameter.  Provide liquidtight flexible conduit in wet and damp locations for equipment subject to vibration, noise transmission, movement or motors.  Provide separate ground conductor across flexible connections.

### 3.1.3   Boxes, Outlets, and Supports

Provide boxes in wiring and raceway systems wherever required for pulling of wires, making connections, and mounting of devices or fixtures.  Boxes for metallic raceways:  cast-metal, hub-type when located in wet locations, when surface mounted on outside of exterior surfaces, and when specifically indicated.  Boxes in other locations:  sheet steel, except that aluminum boxes may be used with aluminum conduit, and nonmetallic boxes may be used with nonmetallic conduit system.  Provide each box with volume required by NFPA 70 for number of conductors enclosed in box.  Boxes for mounting lighting fixtures:  minimum 4 inches square, or octagonal, except that smaller boxes may be installed as required by fixture configurations, as approved.  Boxes for use in masonry-block or tile walls:  square-cornered, tile-type, or standard boxes having square-cornered, tile-type covers.  Provide gaskets for cast-metal boxes installed in wet locations and boxes installed flush with outside of exterior surfaces.  Provide separate boxes for flush or recessed fixtures when required by fixture terminal operating temperature; provide readily removable fixtures for access to boxes unless ceiling access panels are provided.  Support boxes and pendants for surface-mounted fixtures on suspended ceilings independently of ceiling supports.  Fasten boxes and supports with wood screws on wood, with bolts and expansion shields on concrete or brick, with toggle bolts on hollow masonry units, and with machine screws or welded studs on steel.  In open overhead spaces, cast boxes threaded to raceways need not be separately supported except where used for fixture support; support sheet metal boxes directly from building structure or by bar hangers.  Where bar hangers are used, attach bar to raceways on opposite sides of box, and support raceway with approved-type fastener maximum 24 inches from box.  When penetrating reinforced concrete members, avoid cutting reinforcing steel.

#### 3.1.3.1   Boxes

Boxes for use with raceway systems:  minimum 1 1/2 inches deep, except where shallower boxes required by structural conditions are approved.  Boxes for other than lighting fixture outlets:  minimum 4 inches square, except that 4 by 2 inch boxes may be used where only one raceway enters outlet.  Mount outlet boxes flush in finished walls.

#### 3.1.3.2   Pull Boxes

Construct of at least minimum size required by NFPA 70 of code-gauge aluminum or galvanized sheet steel, except where cast-metal boxes are required in locations specified herein.  Provide boxes with screw-fastened covers.  Where several feeders pass through common pull box, tag feeders to indicate clearly electrical characteristics, circuit number, and panel designation.

#### 3.1.3.3   Extension Rings

Extension rings are not permitted for new construction.  Use only on existing boxes in concealed conduit systems where wall is furred out for new finish.

### 3.1.4   Mounting Heights

Mount panelboards, enclosed circuit breakers, motor controller and disconnecting switches so height of operating handle at its highest position is maximum 78 inches above floor.  Mount lighting switches 48 inches above finished floor.  Mount receptacles 18 inches above finished floor, unless otherwise indicated.

### 3.1.5   Conductor Identification

Provide conductor identification within each enclosure where tap, splice, or termination is made.  For conductors No. 6 AWG and smaller diameter, provide color coding by factory-applied, color-impregnated insulation.  For conductors No. 4 AWG and larger diameter, provide color coding by plastic-coated, self-sticking markers; colored nylon cable ties and plates; or heat shrink-type sleeves.

#### 3.1.5.1   Marking Strips

Provide marking strips in accordance with the following:

a.  Provide white or other light-colored plastic marking strips, fastened by screws to each terminal block, for wire designations.

b.  Use permanent ink for the wire numbers

c.  Provide reversible marking strips to permit marking both sides, or provide two marking strips with each block.

d.  Size marking strips to accommodate the two sets of wire numbers.

e.  Assign a device designation in accordance with NEMA ICS 1 to each device to which a connection is made.  Mark each device terminal to which a connection is made with a distinct terminal marking corresponding to the wire designation used on the Contractor's schematic and connection diagrams.

f.  The wire (terminal point) designations used on the Contractor's wiring diagrams and printed on terminal block marking strips may be according to the Contractor's standard practice; however, provide additional wire and cable designations for identification of remote (external) circuits for the Government's wire designations.

g.  Prints of the marking strips drawings submitted for approval will be so marked and returned to the Contractor for addition of the designations to the terminal strips and tracings, along with any rearrangement of points required.

### 3.1.6   Splices

Make splices in accessible locations.  Make splices in conductors No. 10 AWG and smaller diameter with insulated, pressure-type connector.  Make splices in conductors No. 8 AWG and larger diameter with solderless connector, and cover with insulation material equivalent to conductor insulation.

### 3.1.7   Covers and Device Plates

Install with edges in continuous contact with finished wall surfaces without use of mats or similar devices.  Plaster fillings are not permitted.  Install plates with alignment tolerance of 1/16 inch.  Use of sectional-type device plates are not permitted.  Provide gasket for plates installed in wet locations.

### 3.1.8   Electrical Penetrations

Seal openings around electrical penetrations through fire resistance-rated walls, partitions, floors, or ceilings in accordance with Section 07 84 00 FIRESTOPPING.

### 3.1.9   Grounding and Bonding

Provide in accordance with NFPA 70.  Ground exposed, non-current-carrying metallic parts of electrical equipment, metallic raceway systems, grounding conductor in metallic and nonmetallic raceways, telecommunications system grounds, and neutral conductor of wiring systems.  In addition to the requirements specified herein, provide telecommunications grounding in accordance with TIA-607.  Where ground fault protection is employed, ensure that connection of ground and neutral does not interfere with correct operation of fault protection.

#### 3.1.9.1   Ground Rods

Provide cone pointed ground rods.  Measure the resistance to ground using the fall-of-potential method described in IEEE 81.  Do not exceed 25 ohms under normally dry conditions for the maximum resistance of a driven ground.  If this resistance cannot be obtained with a single rod.  If the resultant resistance exceeds 25 ohms measured not less than 48 hours after rainfall, notify the Contracting Officer’s Representative who will decide on the number of ground rods to add.

#### 3.1.9.2   Grounding Connections

Make grounding connections which are buried or otherwise normally inaccessible by exothermic weld or compression connector.

a.  Make exothermic welds strictly in accordance with the weld manufacturer's written recommendations.  Welds which are "puffed up" or which show convex surfaces indicating improper cleaning are not acceptable.  Mechanical connectors are not required at exothermic welds.

b.  Make compression connections using a hydraulic compression tool to provide the correct circumferential pressure.  Provide tools and dies as recommended by the manufacturer.  Use an embossing die code or other standard method to provide visible indication that a connector has been adequately compressed on the ground wire.

#### 3.1.9.3   Ground Bus

Provide a copper ground bus in the electrical equipment rooms as indicated. Noncurrent-carrying metal parts of equipment:  effectively grounded by bonding to the ground bus.  Bond the ground bus to both the entrance ground, and to a ground rod or rods as specified above having the upper ends terminating approximately 4 inches above the floor.  Make connections and splices of the brazed, welded, bolted, or pressure-connector type, except use pressure connectors or bolted connections for connections to removable equipment.

#### 3.1.9.4   Resistance

Maximum resistance-to-ground of grounding system:  do not exceed 5 ohms under dry conditions.  Where resistance obtained exceeds 5 ohms, contact Contracting Officer’s Representative for further instructions.

### 3.1.10   Equipment Connections

Provide power wiring for the connection of motors and control equipment under this section of the specification.  Except as otherwise specifically noted or specified, automatic control wiring, control devices, and protective devices within the control circuitry are not included in this section of the specifications and are provided under the section specifying the associated equipment.

### 3.1.11   Repair of Existing Work

Perform repair of existing work, demolition, and modification of existing electrical distribution systems as follows:

#### 3.1.11.1   Workmanship

Lay out work in advance.  Exercise care where cutting, channeling, chasing, or drilling of floors, walls, partitions, ceilings, or other surfaces is necessary for proper installation, support, or anchorage of conduit, raceways, or other electrical work.  Repair damage to buildings, piping, and equipment using skilled craftsmen of trades involved.

#### 3.1.11.2   Existing Concealed Wiring to be Removed

Disconnect existing concealed wiring to be removed from its source.  Remove conductors; cut conduit flush with floor, underside of floor, and through walls; and seal openings.

#### 3.1.11.3   Removal of Existing Electrical Distribution System

Removal of existing electrical distribution system equipment includes equipment's associated wiring, including conductors, cables, exposed conduit, surface metal raceways, boxes, and fittings, back to equipment's power source as indicated.

#### 3.1.11.4   Continuation of Service

Maintain continuity of existing circuits of equipment to remain.  Maintain existing circuits of equipment energized.  Restore circuits wiring and power which are to remain but were disturbed during demolition back to original condition.

### 3.1.12   Surge Protective Devices

Connect the surge protective devices in parallel to the power source, keeping the conductors as short and straight as practically possible.  Maximum allowed lead length is 3 feet.

## 3.2   FIELD FABRICATED NAMEPLATE MOUNTING

Provide number, location, and letter designation of nameplates as indicated.  Fasten nameplates to the device with a minimum of two sheet-metal screws or two rivets.

## 3.3   WARNING SIGN MOUNTING

Provide the number of signs required to be readable from each accessible side.  Space the signs in accordance with NFPA 70E.

## 3.4   FIELD APPLIED PAINTING

Paint electrical equipment as required to match finish of adjacent surfaces or to meet the indicated or specified safety criteria.  Where field painting of enclosures for panelboards, load centers or the like is specified to match adjacent surfaces, to correct damage to the manufacturer's factory applied coatings, or to meet the indicated or specified safety criteria, provide manufacturer's recommended coatings and apply in accordance to manufacturer's instructions.

## 3.5   FIELD QUALITY CONTROL

Furnish test equipment and personnel and submit written copies of test results.  Give Contracting Officer 5 working days notice prior to each test.

### 3.5.1   Devices Subject to Manual Operation

Operate each device subject to manual operation at least five times, demonstrating satisfactory operation each time.

### 3.5.2   600-Volt Wiring Test

Test wiring rated 600 volt and less to verify that no short circuits or accidental grounds exist.  Perform insulation resistance tests on wiring No. 6 AWG and larger diameter using instrument which applies voltage of approximately 500 volts to provide direct reading of resistance.  Minimum resistance:  250,000 ohms.

### 3.5.3   Ground-Fault Receptacle Test

Test ground-fault receptacles with a "load" (such as a plug in light) to verify that the "line" and "load" leads are not reversed.

### 3.5.4   Grounding System Test

Test grounding system to ensure continuity, and that resistance to ground is not excessive.  Test each ground rod for resistance to ground before making connections to rod; tie grounding system together and test for resistance to ground.  Make resistance measurements in dry weather, not earlier than 48 hours after rainfall.  Submit written results of each test to Contracting Officer, and indicate location of rods as well as resistance and soil conditions at time measurements were made.

-- End of Section --